## 01. ARCH
Pos. | Description of works | Unit | Quantity | Price [MKD] | Total amount [MKD]
1 | PREPARATORY WORKS
1,1 | Site setup and organization according to the site organization scheme provided by the contractor. | lump sum | 1 | 0 | 0
1,3 | Geodetic marking of the object | m2 | 600 | 0 | 0
TOTAL |  |  |  |  | 0
2 | EARTH WORKS
2,1 | Mechanical excavation of soil for laying foundations and slab. The soil classification shall be verified using the Geomechanically Study provided at the construction site by the Investor. The excavation position includes a slope inclination of 45 degrees. Excavation support (shoring) should be taken into account and provided if necessary (as per the opinion of the authorized Supervising Engineer). Transportation to a landfill no further than 20km. | m3 | 280 | 0 | 0
2,2 | Compaction of the soil after excavation in preparation for placing a buffer, leveling, until an appropriate module of compressibility is achieved. | m2 | 657 | 0 | 0
2,3 | Procurement, transport and placement of crushed stone buffer with a total thickness of 60cm (2x30cm), with compaction to the modules of compressibility of 50MPa according to the Project for Building Structures and The Geotechnical Elaborate. The buffer is placed as a fill under the foundations. In all cases according to the graphic attachments and descriptions from the Construction Project. | m3 | 63 | 0 | 0
2,4 | Procurement, transport and placement of crushed stone buffer with a total thickness of 60cm, with compaction to the modules of compressibility of 50MPa according to the Project for Building Structures and The Geotechnical Elaborate. The buffer is placed as a fill under the floor slab and connecting beams. In all cases according to the graphic attachments and descriptions from the Construction Project. | m3 | 208.5 | 0 | 0
2,5 | Procurement and transport, with compaction in layers, of suitable material for backfilling around isolated footings, foundation beams and beneath the floor slab. | m3 | 736 | 0 | 0
TOTAL |  |  |  |  | 0
3 | CONCRETE WORKS
NOTE: Procurement of material, transportation and execution of the concrete and reinforced concrete constructive elements. The execution of all concrete works is with concrete made according to the Macedonian standards and norms for these works and in accordance with the project for Building constructions. All necessary formwork material is included in all positions.
NOTE: In all concrete works planned for the underground levels, a recipe for concrete with the addition of an additive for waterproofing should be taken into account - according to needs. When giving a price for the performance of concrete works for which there is a need to install formwork and scaffolding, the same should be calculated in the appropriate position - mandatory.
3,1 | Procurement of materials, transport and construction of a base of lean concrete with a thickness of 7+5cm and concrete MB20, placed under a foundation slab. | m3 | 48.5 | 0 | 0
3,2 | Procurement of materials, transport and construction of reinforced concrete individual footings with a thickness of 50cm and MB30 concrete, including all necessary formwork. | m3 | 27 | 0 | 0
3,3 | Procurement of materials, transport and construction of reinforced concrete foundation beams with a height of 38cm and concrete MB30, including all necessary formwork. | m3 | 32 | 0 | 0
3,4 | Procurement of materials, transport and construction of a reinforced concrete floor slab with a thickness of 12cm and concrete MB30, including all necessary formwork. | m3 | 65 | 0 | 0
3,5 | Procurement of materials, transport and construction of reinforced concrete slabs with a thickness of 20cm and concrete MB30, including all necessary formwork. | m3 | 4 | 0 | 0
3,6 | Procurement of materials, transport and construction of reinforced concrete columns with dimensions of 40x40cm and MB30 concrete, including all necessary formwork.
3,6,1 | Ground floor, h=364cm | m3 | 14 | 0 | 0
3,6,2 | First floor, h=358cm | m3 | 13.5 | 0 | 0
3,7 | Procurement of materials, transport and construction of reinforced concrete beams with a height of 34cm and concrete MB30, including all necessary formwork.
3,7,1 | Ground floor | m3 | 30 | 0 | 0
3,7,2 | First floor | m3 | 28 | 0 | 0
3,8 | Procurement of materials, transport and construction of a 16cm thick reinforced concrete slab and MB30 concrete,including all necessary formwork.
3,8,1 | First floor | m3 | 96.5 | 0 | 0
3,8,2 | Roof slab | m3 | 89 | 0 | 0
3,9 | Procurement of materials, transport and construction of a reinforced concrete elevator shaft with wall thickness of 20cm and concrete MB30, including all necessary formwork.
3,9,1 | Bottom zone (foundation plate d=30cm) | m3 | 3 | 0 | 0
3,9,2 | Upper zone (plate d=16cm) | m3 | 1.5 | 0 | 0
3,10 | Procurement of materials, transport and construction of internal reinforced concrete stairs, using MB30 concrete, including all necessary formwork. | m3 | 3.5 | 0 | 0
3,11 | Procurement of materials, transport and construction of a reinforced concrete pedestal for VRF-outdoor units for the kitchen, using MB30 concrete, including all necessary formwork. | m3 | 1.08 | 0 | 0
3,12 | Procurement of materials, transport and construction of a reinforced concrete pedestal for a heat pump with a circulation pump, using MB30 concrete, including all necessary formwork. | m3 | 2.23 | 0 | 0
3,13 | Procurement of materials, transport and execution of a lean concrete base with a thickness of 7cm and MB20 concrete, placed under the reinforced concrete pedestal for VRF-outdoor units for the kitchen. | m3 | 0.31 | 0 | 0
3,14 | Procurement of materials, transport and execution of a lean concrete base with a thickness of 7cm and MB20 concrete, placed under the reinforced concrete pedestal for a heat pump with a circulation pump. | m3 | 0.61 | 0 | 0
TOTAL |  |  |  |  | 0
4 | REINFORCEMENT WORKS
4,1 | Procurement of material, transport, stretching, cutting, bending, installation, and tying of B500 ribbed reinforcement, for the performance of concrete works in accordance with the details of the Construction Project.
4,1,1 | to > Ø12 | kg | 11195.22 | 0 | 0
4,1,2 | from ≤ Ø12 | kg | 29234.66 | 0 | 0
4,2 | Procurement of material, transport, stretching, cutting, bending, installation, and tying of Q-335 mesh reinforcement, for the performance of concrete works in accordance with the details of the Construction Project. | kg | 7681.53 | 0 | 0
TOTAL |  |  |  |  | 0
5 | MASONRY WORKS
NOTE: All materials that will be installed must meet the standards and positive legal regulations valid in Macedonia and the EU. All products must be certified and installed as a certified system solution.
5,1 | Procurement of material, transport and masonry of external facade walls made of ceramic blocks with a thickness of 20cm, formation of openings for doors and windows. The price should include all reinforced lintels, horizontal and vertical at the required height where openings for doors and windows are foreseen. | m2 | 546 | 0 | 0
5,2 | Procurement of material, transport and masonry of interior walls made of ceramic blocks with a thickness of 20cm, formation of openings for doors and windows. The price should include all reinforced lintels, horizontal and vertical at the required height where openings for doors and windows are foreseen. | m2 | 423 | 0 | 0
5,3 | Procurement of materials, transport and construction of parapet walls on a roof made of ceramic blocks with a thickness of 20cm, with all necessary reinforced concrete rings with dimensions from the technical drawings. | m2 | 110 | 0 | 0
TOTAL |  |  |  |  | 0
6 | GYPSUM BOARD WORKS
NOTE: All materials that will be installed must meet the standards and positive legal regulations valid in Macedonia and the EU. All products must be certified and installed as a certified system solution.
6,1 | Procurement of material, transport, and installation of partition walls mounted on a single galvanized metal substructure with a profile width of 75mm. The substructure is clad on both sides with double layers of gypsum plasterboards, each 12.5mm thick. The intermediate layer is filled with 5cm of thermal insulation and a 2.5cm air gap. The total thickness of the partition wall is 12.5cm. The price should also include UA profiles for reinforcement at positions where there are openings for doors, glass partitions, and windows, as well as all connecting elements necessary to complete the system. | m2 | 554 | 0 | 0
6,2 | Procurement of material, transport, and installation of moisture-resistant partition walls on one side, mounted on a single galvanized metal substructure with a profile width of 75mm. The substructure is clad on one side with double layers of impregnated (moisture-resistant) gypsum plasterboards, 12.5mm thick, and on the other side with double layers of standard gypsum plasterboards, also 12.5mm thick. The intermediate layer is filled with 5cm of thermal insulation and a 2.5cm air gap. The total thickness of the partition wall is 12.5cm. The price should also include UA profiles for reinforcement at positions where there are openings for doors, glass partitions, and windows, as well as all connecting elements necessary to complete the system. | m2 | 96 | 0 | 0
6,3 | "Procurement of material, transport, and installation of moisture-resistant partition walls mounted on a single galvanized metal substructure with a profile width of 75mm. The substructure is clad on both sides with double layers of impregnated (moisture-resistant) gypsum plasterboards, each 12.5mm thick. The intermediate layer is filled with thermal insulation and an air gap. The total thickness of the partition wall is 12.5cm. This item includes all connecting elements necessary to complete the system. | m2 | 102 | 0 | 0
6,4 | Procurement of material, transport, and installation of fire-resistant partition walls with a fire resistance rating of 120 minutes. The wall is composed of a substructure made of galvanized steel profiles with a width of 75mm. The substructure is clad on both sides with double layers of fire-resistant gypsum plasterboards, type DF (according to MKS EN 520), each 15mm thick. The intermediate layer is filled with 7.5cm of rock wool with a minimum density of 30kg/m³, placed in the voids between the profiles. The joints between the boards are finished in two phases with appropriate gypsum joint filler, and a joint tape is applied on the outer boards. The total thickness of the partition wall is 13.5cm. This item includes all connecting elements necessary to complete the system. | m2 | 18 | 0 | 0
6,5 | Procurement of material, transport, and installation of claddings mounted on a single galvanized metal substructure with a profile width of 50mm. The substructure is clad on one side with three layers of fire-resistant gypsum plasterboards, each 15mm thick, providing a fire resistance duration of 120 minutes. The total thickness of the cladding is 12cm. This item includes all connecting elements necessary to complete the system. | m2 | 13.5 | 0 | 0
6,6 | Procurement of material, transport, and installation of moisture-resistant claddings mounted on a single galvanized metal substructure with a profile width of 50mm. The substructure is clad on one side with two layers of gypsum plasterboards, each 12.5mm thick. The total thickness of the cladding is 7.5cm. This item includes all connecting elements necessary to complete the system. | m2 | 22.5 | 0 | 0
6,7 | Procurement of material, transport, and installation of gypsum plasterboard claddings mounted on a single galvanized metal substructure with a profile width of 50mm. The substructure is clad on one side with two layers of gypsum plasterboards, each 12.5mm thick. The total thickness of the cladding is 7.5cm. This item includes all connecting elements necessary to complete the system. | m2 | 10.5 | 0 | 0
6,8 | Procurement of material, transport, and installation of external cladding for bay windows made of cement boards, each 12.5mm thick, mounted on a single substructure of galvanized metal profiles with dimensions as required by the manufacturer. This item includes all connecting elements necessary to complete the system. | m2 | 55 | 0 | 0
TOTAL |  |  |  |  | 0
7 | CEILING WORKS
NOTE: All materials that will be installed must meet the standards and positive legal regulations valid in Macedonia and the EU. All products must be certified and installed as a certified system solution.
7,1 | Procurement of materials, transport and installation of a suspended ceiling with plasterboard panels with a minimum 30-minute fire resistance. The ceiling has a steel substructure fixed to a reinforced concrete slab. | m2 | 785 | 0 | 0
7,2 | Procurement of materials, transport and installation of a suspended ceiling with perforated steel profiles. The ceiling has a steel substructure fixed to a reinforced concrete slab. | m2 | 58.5 | 0 | 0
TOTAL |  |  |  |  | 0
8 | FLOOR WORKS
NOTE: All materials that will be installed must meet the standards and positive legal regulations valid in Macedonia and the EU. All products must be certified and installed as a certified system solution.
8,1 | Procurement, transport and construction of flooring П1 - OFFICES (ground floor) AND MEDICAL ROOMS (ground floor) 1.THREE-LAYER PARQUET (TARKET) 12.5 mm 2.TARKET ADHESIVE 3.CEMENT SCREED - 7 cm 4.POLYETHYLENE FOIL 5.HARD PRESSED POLYSTYRENE - 8 cm 6.REINFORCED CONCRETE SLAB - 16 cm | m2 | 60 | 0 | 0
8,2 | Procurement, transport and construction of flooring П2 - OFFICES (first floor) 1.THREE-LAYER PARQUET (TARKET) 12.5 mm 2.TARKET ADHESIVE 3.CEMENT SCREED - 7 cm 4.POLYETHYLENE FOIL 5.HARD PRESSED POLYSTYRENE - 2 cm 6.REINFORCED CONCRETE SLAB - 16 cm | m2 | 345.5 | 0 | 0
8,3 | Procurement, transport and construction of flooring П3 - CORRIDORS, STAIRCASE, RESTAURANT (ground floor) 1. CERAMIC TILES - 1 cm 2.TILE ADHESIVE 3.CEMENT SCREED - 4-6 cm 4.POLYETHYLENE FOIL 5.HARD PRESSED POLYSTYRENE - 8 cm 6.REINFORCED CONCRETE SLAB - 16 cm | m2 | 276 | 0 | 0
8,4 | Procurement, transport and construction of flooring П4 - CORRIDOR (first floor) 1.CERAMIC TILES - 1 cm 2.TILE ADHESIVE 3.CEMENT SCREED - 4-6 cm 4.POLYETHYLENE FOIL 5.HARD PRESSED POLYSTYRENE - 2 cm 6.REINFORCED CONCRETE SLAB - 16 cm | m2 | 101 | 0 | 0
8,5 | Procurement, transport and construction of flooring П5 - INDOOR STAIRCASE 1.ARTIFICIEL GRANITE TILES - 2cm 2.TILE ADHESIVE | m2 | 17.5 | 0 | 0
8,6 | Procurement, transport and construction of flooring П6 - KITCHEN, STORAGE (ground floor) 1.CERAMIC TILES - 1 cm, (laid according to H.A.C.C.P.) 2.TILE ADHESIVE 3.CEMENT BASED WATERPROOF COATING, coated in three layers 4.CEMENT SCREED - 4-6 cm 5.POLYETHYLENE FOIL 6.HARD PRESSED POLYSTYRENE - 8 cm 7.REINFORCED CONCRETE SLAB - 16 cm | m2 | 75 | 0 | 0
8,7 | Procurement, transport and construction of flooring П7 - KITCHENETTE (first floor) 1.CERAMIC TILES - 1 cm, (laid according to H.A.C.C.P.) 2.TILE ADHESIVE 3.CEMENT BASED WATERPROOF COATING, coated in three layers 4.CEMENT SCREED - 4-6 cm 5.POLYETHYLENE FOIL 6.HARD PRESSED POLYSTYRENE - 2 cm 7.REINFORCED CONCRETE SLAB - 16 cm | m2 | 25 | 0 | 0
8,8 | Procurement, transport and construction of flooring П8 - TOILETS, TECHNICAL SERVICE (ground floor) 1.CERAMIC TILES - 1 cm 2.TILE ADHESIVE 3.CEMENT BASED WATERPROOF COATING, coated in three layers 4.CEMENT SCREED - 4-6 cm 5.POLYETHYLENE FOIL 6.HARD PRESSED POLYSTYRENE - 8 cm 7.REINFORCED CONCRETE SLAB - 16 cm | m2 | 60.5 | 0 | 0
8,9 | Procurement, transport and construction of flooring П9 - TOILETS (first floor) 1.CERAMIC TILES - 1 cm 2.TILE ADHESIVE 3.CEMENT BASED WATERPROOF COATING, coated in three layers 4.CEMENT SCREED - 4-6 cm 5.POLYETHYLENE FOIL 6.HARD PRESSED POLYSTYRENE - 2 cm 7.REINFORCED CONCRETE SLAB - 16 cm | m2 | 14 | 0 | 0
8,10 | Procurement, transport and construction of flooring П10 - ENTRANCE AREA, TERRACE (ground floor) 1.CERAMIC TILES (for external use) - 1 cm 2.TILE ADHESIVE 3.CEMENT SCREED - 4-6 cm 4.POLYETHYLENE FOIL 5.HARD PRESSED POLYSTYRENE - 8 cm 6.REINFORCED CONCRETE SLAB - 16 cm | m2 | 22.5 | 0 | 0
8,11 | Procurement, transport and construction of flooring П11 - ROOF TERRACE (first floor) 1.ARTIFICIEL GRANITE TILES - 1cm 2.TILE ADHESIVE 0.5-1cm 3.ELASTIC WATER INSULATION 4.CEMENT SLOPE SCREED 5-7cm(0.5%) 5.POLYETHYLENE FOIL 6.POLYMER BITUMEN MEMBRANE WATERPROOFING INSULATION | m2 | 42.5 | 0 | 0
8,12 | Procurement, transport and installation of wooden skirting boards for tarket flooring, with dimensions 60х16х2400 mm | m' | 311 | 0 | 0
8,13 | Procurement, transport and installation of transitional aluminium profiles, with dimensions 30х2700 mm | m' | 12 | 0 | 0
TOTAL |  |  |  |  | 0
9 | PLASTERING WORKS
NOTE: All materials that will be installed must meet the standards and positive legal regulations valid in Macedonia and the EU. All products must be certified and installed as a certified system solution.
9,1 | Procurement of materials, transport and plastering of internal vertical surfaces with gypsum plaster in two layers (first layer coarse plastering and second layer fine plastering) with a total thickness of 1-2cm and in accordance with the manufacturer's instructions. This position should also include galvanized corner strips for corner protection. This position foresees the use of mobile scaffolding. | m2 | 1712.5 | 0 | 0
TOTAL |  |  |  |  | 0
10 | PAINTING WORKS
NOTE: All materials that will be installed must meet the standards and positive legal regulations valid in Macedonia and the EU. All products must be certified and installed as a certified system solution.
10,1 | Procurement of material, transport and smoothing of vertical interior surfaces. Before starting smoothing, the surface should be coated with a smoothing base. This position requires the use of mobile scaffolding. | m2 | 2539 | 0 | 0
10,2 | Procurement of material, transport and smoothing of horizontal interior surfaces (ceilings). Before starting smoothing, the surface should be coated with a smoothing base. This position requires the use of mobile scaffolding. | m2 | 115 | 0 | 0
10,3 | Procurement of material, transport and painting of vertical interior surfaces. Painting shall be carried out with dispersion paint made on the basis of water dispersions, applied in two layers, with a color of the Investor's choice. Before starting painting, the surface should be coated with a paint base. This position envisages the use of mobile scaffolding. | m2 | 2539 | 0 | 0
10,4 | Procurement of material, transport and painting of horizontal interior surfaces (ceilings). Painting shall be carried out with dispersion paint made on the basis of water dispersions, applied in two layers, with a color of the Investor's choice. Before starting painting, the surface should be coated with a paint base. This position envisages the use of mobile scaffolding. | m2 | 115 | 0 | 0
TOTAL |  |  |  |  | 0
11 | CERAMIC WORKS
NOTE: All materials that will be installed must meet the standards and positive legal regulations valid in Macedonia and the EU. All products must be certified and installed as a certified system solution.
11,1 | Procurement of material, transport and installation of wall ceramic tiles (I class) with a minimum thickness of 0.7cm applied to the height of the suspended ceiling. The position also includes tile adhesive, the necessary internal, external and final metal corner strips and filling the joints with grout. The method of stacking and grouting is at the discretion of the Investor. The quantity is with a calculated spread of 10%. | m2 | 484 | 0 | 0
11,2 | Procurement of material, transport and installation of wall ceramic tiles (I class) with a minimum thickness of 0.7cm applied to the height of a suspended ceiling. The position also includes tile adhesive, the necessary internal, external and final metal corner strips and filling the joints with grout. The method of stacking and grouting is at the discretion of the Investor. The quantity is calculated with a 10% spread. Note: The tiles are intended for the kitchen and should be installed in accordance with the HACCP system. | m2 | 200 | 0 | 0
11,3 | Procurement, transport and production of ceramic tile skirting boards with a thickness of 0.7cm, with a height of 15cm around the perimeter of the premises planned to have a ceramic tile floor. The item includes tile adhesive, grouting of the joints and corner aluminum moldings. The quantity is calculated with a 10% spread. | m' | 285.5 | 0 | 0
11,4 | Coating of walls with a dust-proofing and adhesion-enhancing primer as preparation for tile installation. | m2 | 684 | 0 | 0
TOTAL |  |  |  |  | 0
12 | INSULATION WORKS
NOTE: All materials that will be installed must meet the standards and positive legal regulations valid in Macedonia and the EU. All products must be certified and installed as a certified system solution.
NOTE: The waterproofing in the underground layers must be offered as a system certified solution in all its parts, with all necessary certificates. Before construction, the waterproofing solution must be offered and presented to the supervisor and the investor. The system solution should include the works for securing (horizontal and vertical waterproofing) in the underground levels, to provide adequate protection during the entry - penetration of installations and interruptions of concreting.
12,1 | Procurement of material, transport and installation of a vapor barrier, three-layer reinforced and resistant to tearing and aging. The installation of the rolls should be with an overlap of 10cm and a vertical rise along the wall and installations of 10cm. The overlap of the rolls as well as the penetrations of installations should be closed with aluminum adhesive tape along the entire length. | m2 | 526.5 | 0 | 0
12,2 | Procurement of materials, transport, preparation and installation of a three-layer highly vapor-permeable waterproof roofing membrane, consisting of 2 polypropylene fabrics and a functional polypropylene layer that provides water vapor permeability and water resistance. The waterproofing should be installed with an overlap of at least 10cm. | m2 | 530 | 0 | 0
12,3 | Procurement of material, transport and installation of roof thermal insulation made of stone wool with a density of 30kg/m³ and a total thickness of 20cm, laid in two layers of 10 and 10cm. | m2 | 549.5 | 0 | 0
12,4 | Procurement of material, transport, and installation of extruded polystyrene (XPS) with a thickness of 2 cm and a density of 30–40 kg/m³, applied to the external side of the foundations as protection for the waterproofing. The thermal insulation must be installed in accordance with the manufacturer's instructions | m2 | 348.5 | 0 | 0
12,5 | Procurement of material, transport, and installation of vertical waterproofing using an elastomeric waterproofing membrane made of high-quality bituminous compound enriched with elastomers (SBS) and reinforced with polyester felt, with a thickness of 3–5 mm. The membrane is applied over a previously cleaned substrate primed with a bitumen- and solvent-based primer. The bituminous membrane is installed by full-surface torch welding with 10 cm overlaps. The waterproofing must be installed in accordance with the manufacturer's instructions. | m2 | 518 | 0 | 0
12,6 | Procurement of material, transport, and installation of horizontal waterproofing using an elastomeric waterproofing membrane made of high-quality bituminous compound enriched with elastomers (SBS) and reinforced with polyester felt, with a thickness of 3–5 mm. The membrane is applied over a previously cleaned substrate primed with a bitumen- and solvent-based primer. The bituminous membrane is installed by full-surface torch welding with 10 cm overlaps. The waterproofing must be installed in accordance with the manufacturer's instructions. | m2 | 524 | 0 | 0
12,7 | Procurement of materials, transport and installation of two-component elastic rubber-based waterproofing applied in three layers on the wall surface in the kitchen and sanitary facilities (wet areas). The installation of the waterproofing should be carried out in accordance with the manufacturer's instructions. | m2 | 571 | 0 | 0
12,8 | Procurement of materials, transport, and installation of polyethylene foil used as a vapor barrier to isolate from evaporation. To be installed at an elevation of +4.24. | m2 | 42.5 | 0 | 0
12,9 | Procurement of materials, transport and installation of two-component elastic waterproofing on the floor surface of a roof terrace. The installation of the waterproofing should be carried out in accordance with the manufacturer's instructions. | m2 | 42.5 | 0 | 0
12,10 | Procurement of material, transport and installation of ceiling thermal insulation made of rock wool with a density of 130kg/m³ and a total thickness of 20cm, stacked in two layers of 10 and 10cm, screwed with dowels. | m2 | 21.5 | 0 | 0
TOTAL |  |  |  |  | 0
13 | CARPENTRY WORKS
13,1 | Procurement of materials, transport and installation of OSB boards as the final floor covering of the building with a thickness of 15mm with all necessary joints with the wooden structure. | m2 | 526.5 | 0 | 0
13,2 | Procurement of material, fabrication, transport, and installation of a wooden substructure for the placement of the roof covering. The substructure is made of wooden battens with dimensions of 5/3cm, installed in two directions—the first layer at a center-to-center spacing of 55cm, and the second layer also at 55cm spacing. This item includes all necessary connecting elements. | m3 | 3.5 | 0 | 0
13,3 | "Procurement of material, transport, fabrication, and installation of a wooden roof structure (simple truss) made of pine timber, including posts with dimensions of 10x10cm, beams with dimensions of 10x12cm, and rafters with dimensions of 10x12cm, all first-class quality. All joints between the wooden structural elements of the roof shall be executed according to traditional carpentry methods, using wedges, screws, and all other necessary steel reinforcement elements. The work also includes installation of steel anchors into the reinforced concrete structure and fixing of the roof timber to the reinforced concrete structure. Anchors must be protected with an anti-corrosion coating. The timber must be coated with a non-washable impregnating agent designed for long-term preventive protection of wooden roof structures against wood-damaging pests. | m3 | 12 | 0 | 0
TOTAL |  |  |  |  | 0
14 | ROOFING WORKS
14.1 | Procurement of material, transport, cutting, and installation of final roofing made of ribbed, trapezoidal, plastic-coated steel sheet metal with a thickness of 0.6mm, for the execution of roofing works on the gable roof of the building. This item includes all necessary connecting elements. The color of the sheet metal shall be selected by the investor. | m2 | 537.5 | 0 | 0
14.2 | Procurement of material, cutting, transport, and installation of flat, plastic-coated steel sheet metal for roof flashings, with a thickness of 0.6mm. The sheet metal is to be installed in various positions, with varying developed widths depending on the installation detail. This item includes all necessary connecting elements. The color of the sheet metal shall be selected by the investor.
14,2,1 | Ridge capping with a width of 30cm | m' | 31.5 | 0 | 0
14,2,2 | Cladding on a parapet wall with a width of 50cm | m' | 102.5 | 0 | 0
14,2,3 | Attic and pitched roof cladding with a width of 30cm | m' | 47 | 0 | 0
TOTAL |  |  |  |  | 0
15 | SHEET STEEL WORKS
15,1 | Procurement of material, transport, fabrication, and installation of vertical gutters with a square cross-section of 16x16cm, made of plastic-coated steel sheet metal with a thickness of 0.6mm, sealed using machine crimping. The item includes all necessary fastening materials, elbows, and required brackets. The color of the sheet metal shall be selected by the investor. | m' | 36.5 | 0 | 0
15,2 | Procurement of material, transport, fabrication, and installation of vertical gutters with a square cross-section of 10x10cm, made of plastic-coated steel sheet metal with a thickness of 0.6mm, sealed using machine crimping. The item includes all necessary fastening materials, elbows, and required brackets. The color of the sheet metal shall be selected by the investor. | m' | 13 | 0 | 0
15,3 | Procurement of material, transport, fabrication, and installation of horizontal gutters with dimensions of 15x12cm and a developed width of 80cm, made of plastic-coated steel sheet metal with a thickness of 0.6mm. The item includes all necessary fastening materials, required brackets, corners, and covers. The color of the sheet metal shall be selected by the investor. | m' | 69 | 0 | 0
15,4 | Procurement of material, transport, fabrication, and installation of collector pots for the transition from horizontal gutter to vertical gutter. | piece | 6 | 0 | 0
15,5 | Procurement of material, transport, and installation of an initial aluminum trim fixed with screws at the base of the wall around the perimeter of the building. The trim serves as support for the first layer of 10cm thick stone wool boards. | m' | 97.5 | 0 | 0
15,6 | Procurement of material, transport, and installation of a final aluminum trim with a drainage edge, fixed with screws at the top of the insulation system. This trim serves to close the system and prevent water penetration.. | m' | 105 | 0 | 0
TOTAL |  |  |  |  | 0
16 | LOCKSMITH WORKS
16,1 | Procurement of material, fabrication, transport, and installation of a steel protective fence for terraces, with a height of 100cm. The fence is made of vertical rectangular profiles 40/40mm, horizontal rectangular profiles 40/10mm, and vertical segments made from rectangular profiles 40/1mm, placed at a distance of 8.5cm. The fence is anchored with anchor plates 80/80/5mm and screws to the reinforced concrete slab. The structure must be galvanized and coated with anti-corrosion protection, and finally painted with acrylic paint. Prior to fabrication, measurements should be verified on-site. | m' | 15 | 0 | 0
16,2 | Procurement of material, fabrication, transport, and installation of a steel protective fence for stairs, with a height of 105cm. The fence is made of vertical rectangular profiles 40/40mm, horizontal rectangular profiles 40/10mm, and vertical segments made from rectangular profiles 40/1mm, placed at a distance of 8.5cm. The fence is anchored with anchor plates 80/80/5mm and screws to the reinforced concrete slab. The structure must be galvanized and coated with anti-corrosion protection, and finally painted with acrylic paint. Prior to fabrication, measurements should be verified on-site. | m' | 7 | 0 | 0
TOTAL |  |  |  |  | 0
17 | FACADE WORKS
17,1 | Procurement of material, transport, and installation of a vertical contact facade made from materials that have an ETA certificate, in accordance with all technical regulations for the execution of this type of work.
1. Vapour-permeable adhesive based on cement, specially formulated for stone wool. The adhesive has high adhesion and is resistant to mechanical stresses and temperature changes. The vapour permeability prevents moisture accumulation.
2. Thermal insulation board made of stone wool with a density of 130-160 kg/m³ and a thickness of 10cm, complete with metal anchors for fastening.
3. Wire mesh (fiberglass fabric), alkali-resistant, in accordance with the ETICS system, resistant to cracking and impact, along with bonding layers that will be elastic, resistant to stresses, cracking, and mechanical damage.
4. Final layer of structural acrylic plaster based on synthetic resins and solvents, applied in three layers (color selected by the investor), resistant to atmospheric influences, dirt, elastic, and durable against mechanical impact. The color is specified in the graphical attachments from the architecture.
At all right angles on the facade, including those around the window openings, PVC corner trims with mesh shall be used.
| Total | m2 | 913 | 0 | 0
17,2 | Procurement of material, transport, and installation of a horizontal contact facade made from materials that have an ETA certificate, in accordance with all technical regulations for the execution of this type of work.
1. Vapour-permeable adhesive based on cement, specially formulated for stone wool. The adhesive has high adhesion and is resistant to mechanical stresses and temperature changes. The vapour permeability prevents moisture accumulation.
2. Thermal insulation board made of stone wool with a density of 130-160 kg/m³ and a thickness of 10cm, complete with metal anchors for fastening.
3. Wire mesh (fiberglass fabric), alkali-resistant, in accordance with the ETICS system, resistant to cracking and impact, along with bonding layers that will be elastic, resistant to stresses, cracking, and mechanical damage.
4. Final layer of structural acrylic plaster based on synthetic resins and solvents, applied in three layers (color selected by the investor), resistant to atmospheric influences, dirt, elastic, and durable against mechanical impact. The color is specified in the graphical attachments from the architecture.
At all right angles on the facade, including those around the window openings, PVC corner trims with mesh shall be used.
| Total | m2 | 55 | 0 | 0
17,3 | Procurement, transport, and installation of reveals and lintels around the window openings made of stone wool with a density of 130-160 kg/m³ and a thickness of 2cm. The contact facade is composed of materials with an ETA certificate, in accordance with all applicable technical regulations for the execution of this type of work. This position also includes all other components required to complete the contact facade, as specified in position 18.1. | m' | 288 | 0 | 0
17,4 | Drip edges made of artificial granite tiles with a width of 15cm. | m' | 43.5 | 0 | 0
17,5 | Sills made of artificial granite tiles with a width of 35cm and 15cm.. | m' | 34.5 | 0 | 0
17,6 | Transport and installation of facade scaffolding. The scaffolding should have installed dismantling platforms, covering with fabric or PVC protective cover platforms above the entrances, as well as informational warning signs. (The scaffolding should be constructed in accordance with instructions and regulations, and safety measures during work should be implemented), with dismantling after the completion of the construction works. | m2 | 885.5 | 0 | 0
TOTAL |  |  |  |  | 0
18 | WINDOWS AND DOORS
FACADE CARPENTRY
18,1 | Procurement of material, transport, and installation of windows made from 5-chamber PVC profiles (with a solved thermal bridge). Glazing with double-layer thermopan glass with a thickness of 4+16+4mm, filled with argon, and with a maximum heat transfer coefficient of Uw=1.1 W(m²K). The seals are made of EPDM rubber, machine-rolled at the factory. The windows are equipped with standard hardware according to the intended use. The color of the profiles is anthracite RAL 7016. Details according to the joinery schematic.
18,1,1 | POS. П1 dimensions 90/230cм | piece | 1 | 0 | 0
18,1,2 | POS. П2 dimensions 90/230cм | piece | 7 | 0 | 0
18,1,3 | POS. П2' dimensions 90/230cм | piece | 7 | 0 | 0
18,1,4 | POS. П3 dimensions 90/130cм | piece | 3 | 0 | 0
18,1,5 | POS. П4 dimensions 180/130cм | piece | 1 | 0 | 0
18,1,6 | POS. П5 dimensions 270/130cм | piece | 1 | 0 | 0
18,1,7 | POS. П6 dimensions 180/230cм | piece | 10 | 0 | 0
18,1,8 | POS. П6' dimensions 180/230cм | piece | 10 | 0 | 0
18,1,9 | POS. НВ1 dimensions 180/230cм | piece | 3 | 0 | 0
18,1,10 | POS. НВ2 dimensions 360/230cм | piece | 4 | 0 | 0
EXTERIOR DOORS
18,2 | Procurement of material, transport, and installation of an external single-leaf door B4 with dimensions 100/210cm. The frame and door leaf are made of galvanized steel profiles. The opening system is with hinges with ball bearings. The door is equipped with a cylinder lock with three keys and a double-sided handle, with the door leaf opening at an angle of 90°. Details according to the joinery schematic.
18,2,1 | POS. В4 dimensions 100/210cм | piece | 1 | 0 | 0
FIRE RESISTANCE DOORS
18,3 | Procurement of materials, manufacturing, transportation and installation of a single-leaf fire door with a fire resistance of 90 minutes. The frame and door leaf are made of galvanized steel profiles. The opening system is with ball bearing hinges. The door is equipped with a cylinder lock with three keys and a double-sided handle, with the wings opening at an angle of 90°. The position is provided with an expanding strip when in contact with the wall surface.
18,3,1 | POS. ПП1 dimensions 180/210cм | piece | 2 | 0 | 0
18,4 | Procurement of material, fabrication, transport, and installation of a single-leaf fire door with a fire resistance of 120 minutes. The frame and door leaf are made of galvanized steel profiles. The opening system is with hinges with ball bearings. The door is equipped with a handle on one side and a PANIC BAR (in the direction of evacuation), with the door leaf opening at an angle of 90°. It includes a self-closing mechanism and a magnetic holder for the open position (x2). The position includes cladding with an expanding seal at the contact with the wall surface.
18,4,1 | POS. ПП2 dimensions 110/210cм | piece | 4 | 0 | 0
18,5 | Procurement of material, fabrication, transport, and installation of a single-leaf fire door with a fire resistance of 120 minutes. The frame and door leaf are made of galvanized steel profiles. The opening system is with hinges with ball bearings. The door is equipped with standard hardware for its intended purpose and a double-sided handle, with the door leaf opening at an angle of 90°. The position includes cladding with an expanding seal at the contact with the wall surface.
18,5,2 | POS. ПП3 dimensions 100/210cм | piece | 6 | 0 | 0
INTERIOR DOORS
18,6 | Procurement of material, fabrication, transport, and installation of internal single-leaf doors. The frame and door leaf shall be made of medium-density fiberboard (MDF), filled with honeycomb core and double-sided MDF cladding. The opening system uses hinges with ball bearings. The doors are equipped with standard hardware according to their intended use and a double-sided steel handle. Details according to the joinery scheme.
18,6,1 | POS. В1 dimensions 100/210cм | piece | 23 | 0 | 0
18,6,2 | POS. В2 dimensions 80/210cм | piece | 9 | 0 | 0
DOOR FOR PEOPLE WITH DISABILITIES
18,7 | Procurement of material, fabrication, transport, and installation of internal single-leaf doors. The frame and door leaf shall be made of medium-density fiberboard (MDF), filled with a honeycomb core and double-clad with MDF. The opening system uses hinges with ball bearings. The doors are equipped with standard hardware according to their intended use and a double-sided steel handle. Details according to the joinery scheme.
18,7,1 | POS. В3 dimensions 110/210cм | piece | 1 | 0 | 0
INTERIOR GLASS PARTITIONS
18,8 | Procurement of material, transport, and installation of internal glass doors/partitions made from plastic-coated aluminum profiles (without thermal bridge resolution). The glazing is done with double-layer laminated glass. The partitions are equipped with standard hardware according to their intended use. The color of the profiles is anthracite RAL 7016. Details according to the joinery scheme.
18,8,1 | POS. ВСП1 dimensions 375/230cм | piece | 2 | 0 | 0
18,8,2 | POS. ВСП2 dimensions 180/230cм | piece | 1 | 0 | 0
18,8,3 | POS. ВСП3 dimensions 393/230cм | piece | 2 | 0 | 0
18,8,4 | POS. ВСП4 dimensions 406/230cм | piece | 1 | 0 | 0
18,8,5 | POS. ВП1 dimensions 180/130cм | piece | 1 | 0 | 0
PARTITIONS IN TOILETS
18,9 | Partition with single door, internal partition system for toilets made from compact HPL panel with thickness of 10mm, 100% waterproof, fire-resistant, scratch-resistant, abrasion-resistant, and resistant to cleaning agents. The solution is complete with all necessary hardware. Details according to the joinery scheme.
18,9,1 | POS. ПР1 dimensions 120/210; 202/180cм | piece | 2 | 0 | 0
18,9,2 | POS. ПР2 dimensions 180/210cм | piece | 1 | 0 | 0
18,9,3 | POS. ПР3 dimensions 210/210cм | piece | 1 | 0 | 0
18,9,4 | POS. ПР4 dimensions 133/210cм | piece | 1 | 0 | 0
18,9,5 | POS. ПР5 dimensions 180/210cм | piece | 2 | 0 | 0
TOTAL |  |  |  |  | 0
19 | OTHER WORK
19,1 | Procurement, transportation, and installation of an elevator with 2 stations, capacity of 1000 kg, speed of 1m/s, fire-resistant doors, and designed in accordance with the current regulations for vertical transport for people with disabilities. The contractor is also required to calculate the scaffolding necessary for the equipment installation and painting of the elevator shafts according to the standards for equipment installation. The elevator doors are sliding from one side. The contractor should prepare the necessary technical documentation for the installation of the elevator (elevator project). | piece | 1 | 0 | 0
TOTAL |  |  |  |  | 0
RECAPITULATION
Construction and Construction-Craft Works
No. of pos. | Description of position |  |  |  | Total Price
1 | PREPARATORY WORKS |  |  |  | 0
2 | EARTH WORKS |  |  |  | 0
3 | CONCRETE WORKS |  |  |  | 0
4 | REINFORCEMENT WORKS |  |  |  | 0
5 | MASONRY WORKS |  |  |  | 0
6 | GYPSUM BOARD WORKS |  |  |  | 0
7 | CEILING WORKS |  |  |  | 0
8 | FLOOR WORKS |  |  |  | 0
9 | PLASTERING WORKS |  |  |  | 0
10 | PAINTING WORKS |  |  |  | 0
11 | CERAMIC WORKS |  |  |  | 0
12 | INSULATION WORKS |  |  |  | 0
13 | CARPENTRY WORKS |  |  |  | 0
14 | ROOFING WORKS |  |  |  | 0
15 | STEEL SHEET WORKS |  |  |  | 0
16 | LOCKSMITH WORKS |  |  |  | 0
17 | FACADE WORKS |  |  |  | 0
18 | WINDOWS AND DOORS |  |  |  | 0
19 | OTHER WORKS |  |  |  | 0
Subtotal (MKD) |  |  |  |  | 0
18% VAT (MKD) |  |  |  |  | 0
Grand total (MKD) |  |  |  |  | 0
Prepared by
Andrej Proshevski, M.Arch.
__________________________

## 02. ELEC
No | SCOPE OF WORK | Unit of measure | Quantity | Unit price (MKD) | TOTAL (MKD)
Note: For all descriptions referring to manufacturers or standards, the term "equivalent" applies. This means that the product or material offered as a substitute must have the same or better technical characteristics as those specified in the original description. This applies to all items in the bill of quantities. Furthermore, the contractor may propose equivalent solutions that achieve the same or similar performance in order to obtain more efficient and optimized results.
HIGH VOLTAGE INSTALLATION-ADMINISTRATIVE BUILDING
1 | POWER CABLES AND DISTRIBUTION BOARDS
With each cabinet/distribution panel, a certificate for type-tested cabinet/distribution panel, electrical equipment, a test report, and a certificate from the manufacturer for the license as an authorized Panel Builder in accordance with IEC 61439-2, and in compliance with RoHS directives, shall be provided. The cabinet/distribution panel shall be assembled according to the project documentation.
1.1 | Procurement, transportation, and installation of a distribution cabinet, wall-mounted (surface-mounted), modular design, electrostatically painted in RAL 7035, according to standards IEC/EN 62208, IEC/EN 60529, IEC/EN 62262, type-tested and assembled according to IEC 61439-2 standard, and compliant with RoHS directives. Installed in the ground floor corridor, according to the position shown in the graphic attachments, and equipped with the following: GRT-Adm_m 1 piece. Three-pole automatic circuit breaker 630A with magnetic and thermal release and remote trip switch with In=400A 1 pair. Three-pole automatic circuit breaker 250A with magnetic and thermal release and remote trip switch with In=250A 3 pairs. High-performance fuses NPOO400/NVO315 A, 1p 10 pairs. Automatic circuit breaker B16A, 1p 1 pair. Automatic circuit breaker C63A, 3p 1 pair. Automatic circuit breaker C40A, 3p 4 pairs. Automatic circuit breaker C20A, 3p 1 pair. Automatic circuit breaker C25A, 3p 4 pairs. Automatic circuit breaker C16A, 1p 1 pair. Automatic circuit breaker C10A, 1p 1 pair. RCD switch 25A, 2p, 0.03A 1 pair. Motor protection switch: 16A, 2p with bimetal (2.5-4)A 1 pair. Motor protection switch: 16A, 2p with bimetal (1-1.6)A 7 pairs. Three-phase 63A control and measuring meter Surge arrester with integrated automatic switch, modular surge arrester - 3 poles + N - 350V type T1+T2 - with remote transfer 1 pair. Single-line diagram in plastic pocket 20% spare capacity Small unspecified materials | piece | 1 | 0 | 0
1.2 | Procurement, transport, and installation of a modular wall-mounted distribution board (flush or surface-mounted), with IP40 protection, built-in terminal blocks for PE and N, transparent door, fully compliant with IEC 60670-24 standard. The board shall be mounted at a height of 1.8 meters and include the following built-in equipment: DB-Kitchen_M (РТ-Кујна-М) -1 pc three-pole circuit breaker, 400A, with magnetic and thermal release, and remote trip switch, In = 315A -1 pc miniature circuit breaker B10A, 1-pole -10 pcs miniature circuit breaker C16A, 1-pole -23 pcs miniature circuit breaker B16A, 1-pole -2 pcs miniature circuit breaker B63A, 3-pole -3 pcs miniature circuit breaker B40A, 3-pole -3 pcs miniature circuit breaker B25A, 3-pole -2 pcs miniature circuit breaker C50A, 3-pole -2 pcs miniature circuit breaker C20A, 3-pole -1 pc residual current device (RCD), 25A, 4-pole, 30mA -1 pc single-line diagram in a plastic pocket 20% spare space Miscellaneous unspecified small materials | piece | 1 | 0 | 0
1.3 | Procurement, transportation, and installation of a distribution board cabinet, modular type for wall mounting, with IP40 protection rating, equipped with built-in terminal blocks for PE and N, with transparent door, fully compliant with IEC 60670-24 standard. Mounted at a height of 1.8 m with the following built-in equipment: RT-Adm1_M (РТ-Адм.1-М) 1 pc. busbar switch 63A, 3p, 1-0 6 piece miniature circuit breaker B10A, 1p 6 piece miniature circuit breaker C16A, 1p 38 piece miniature circuit breaker B16A, 1p 3 piece bistable relay 10A, 1p 1 pc. RCD switch 25A, 4p, 0.03A1 pc. RCD switch 40A, 4p, 0.03A 1 pc. single-line diagram in plastic pocket 20% spare space Small unspecified material | piece | 1 | 0 | 0
1.4 | Procurement, transport, and installation of a wall-mounted (surface-mounted) modular distribution cabinet, electrostatically powder-coated RAL 7035, compliant with IEC/EN 62208, IEC/EN 60529, IEC/EN 62262 standards, type tested and assembled according to IEC 61439-2 standard, and in accordance with RoHS directives. Installed in the ground floor corridor according to the position in the graphic attachments, with the following equipment: DGRТ-Adm_A (ДГРТ-Адм.-А) -1 pc three-pole circuit breaker 63A with magnetic and thermal release and remote trip switch, In = 32A -5 pcs miniature circuit breaker B10A, 1-pole -4 pcs miniature circuit breaker B16A, 1-pole -3 pcs miniature circuit breaker C20A, 3-pole -3 pcs three-phase 63A direct control measuring meter for DIN rail mounting -Surge arrester with integrated automatic circuit breaker, modular surge arrester – 3 poles + N – 350V, Type T1+T2, with remote signaling -1 pc single-line diagram in a plastic pocket 20% spare space Miscellaneous unspecified small materials | piece | 1 | 0 | 0
1.5 | Procurement, transportation, and installation of distribution board modules for wall mounting, with IP40 protection, equipped with terminal blocks for PE and N, with transparent door, all according to IEC60670-24 standard. Mounted at a height of 1.8 m with the possibility to install modular equipment: RT-1/2/3/4/5, RT-Ambulance | piece | 6 | 0 | 0
1.6 | Procurement, transport, and installation of a distribution board module for wall mounting, with IP40 protection, equipped with built-in terminal blocks for PE and N, with a transparent door, all according to IEC60670-24 standard. Installed at a height of 1.8 m with the following built-in equipment: DRT-Kitchen_A 1 pc. busbar comb switch 20A, 3p, 1-0 4 piece miniature circuit breaker B10A 2 piece miniature circuit breaker B16A, 1p 1 pc. single-line diagram in plastic pocket 20% spare space Small unspecified materials | piece | 1 | 0 | 0
1.7 | Procurement, transport, and installation of a distribution board module for wall mounting, with IP40 protection, equipped with built-in terminal blocks for PE and N, with a transparent door, all according to IEC60670-24 standard. Installed at a height of 1.8 m with the following built-in equipment: DRT-Adm1_A 1 pc. busbar comb switch 20A, 3p, 1-0 6 piece miniature circuit breaker B10A 1 pc. miniature circuit breaker B16A, 1p 3 piece bistable relay 10A, 1p 1 pc. single-line diagram in plastic pocket 20% spare space Small unspecified materials | piece | 1 | 0 | 0
1.8 | Procurement, transport, and installation of a distribution board module for wall mounting, with IP40 protection, equipped with built-in terminal blocks for PE and N, with a transparent door, all according to IEC60670-24 standard. Installed at a height of 1.8 m with the following built-in equipment: RT-Hauba 1 1 pc. busbar comb switch 20A, 3p, 1-0 for cover mounting 1 pc. miniature circuit breaker B10A 1 pc. motor protection switch: 16A, 2p with bimetal (4-6.3)A 1 pc. contactor 1NO/1NC 16A, 1p Small unspecified materials | piece | 1 | 0 | 0
1.9 | Procurement, transport, and installation of a distribution board module for wall mounting, with IP40 protection, equipped with built-in terminal blocks for PE and N, with a transparent door, all according to IEC60670-24 standard. Installed at a height of 1.8 m with the following built-in equipment: RT-Hauba 2 1 pc. busbar comb switch 20A, 3p, 1-0 for cover mounting 1 pc. miniature circuit breaker B10A 1 pc. motor protection switch: 16A, 4p with bimetal (0.63-1)A 1 pc. contactor 1NO/1NC 16A, 3p Small unspecified materials | piece | 1 | 0 | 0
1.1 | PVC rigid conduit Ø100mm, length 3m, for building entry | piece | 2 | 0 | 0
1.11 | Rigid HDPE pipe Ø110mm, for installation crossing under the road | m | 20 | 0 | 0
1.12 | Excavation of trench with dimensions 0.8 x 0.4 m, complete with backfilling and compaction of soil with sand and plastic protective tube along the entire length | m | 170 | 0 | 0
1.13 | Supply and installation of a power cable from the metering distribution cabinet located near the transformer station to the main distribution board GRT-Adm_m Cable jointing according to energy approval, complete with all necessary materials. Cable type: 4x(2x(NYY-J-1x120mm²)) + NYY-J-1x120mm². The conductor is mostly routed underground in a trench. Payment is made per meter, complete and obligatory. | m | 180 | 0 | 0
1.14 | Supply and installation of a power cable from the metering distribution cabinet located next to the diesel generator to the main distribution board DGRT-Adm_A. Cable jointing according to energy approval, complete with all necessary materials. Cable type: NYY-J-5x6mm². The conductor is mostly routed underground in a trench. Payment is made per meter, complete and obligatory. | m | 180 | 0 | 0
1.15 | Supply and installation of a power cable from GRT-Adm_M to distribution board RT-Adm1_m Cable jointing complete with all necessary materials. Cable type: N2XH-J-5x16mm². The cable is routed on cable trays. Payment is made per meter, complete and obligatory. | m | 30 | 0 | 0
1.16 | Procurement and installation of power-supplied cable from GRT-Adm_M to distribution panel RT-1/2/3/4/5. Complete cable connection including all necessary components, using cable type N2XH-J-5x4mm². The cable is routed on cable trays. Payment is calculated per linear meter for the complete setup. | m | 100 | 0 | 0
1.17 | Procurement and installation of power-supplied cable from GRT-Adm_M to distribution panel RT-Ambulance. Complete cable connection including all necessary components, using cable type N2XH-J-5x10mm². The cable is routed on cable trays. Payment is calculated per linear meter for the complete setup. | m | 20 | 0 | 0
1.18 | Procurement and installation of power-supplied cable from GRT-Adm_M to kitchen distribution panel RT-Kitchen-m Complete cable connection including all necessary components, using cable type 4x(2x(N2XH-J-1x70mm²)) + N2XH-J-1x70mm². The cable is routed on cable trays. Payment is calculated per linear meter for the complete setup. | m | 30 | 0 | 0
1.19 | Procurement and installation of power-supplied cable from GRT-Kitchen_M to kitchen hood distribution panel RT-Hood.1/2. Complete cable connection including all necessary components, using cable type N2XH-J-5x4mm². The cable is routed along the wall beneath the plaster. Payment is calculated per linear meter for the complete setup. | m | 40 | 0 | 0
1.2 | Procurement and installation of power-supplied cable from DGRT-Adm_A to distribution panels DRT-Kitchen_A and DRT-Adm1. Complete cable connection including all necessary components, using cable type N2XH-J-5x4mm² (FE180E90). The cable is routed on cable trays. Payment is calculated per linear meter for the complete setup. | m | 50 | 0 | 0
| Total: |  |  |  | 0
2 | ELECTRICAL INSTALLATIONS FOR LIGHTING
2.1 | Procurement, delivery and laying of conductors for the installation of lighting points of the following type: NHXMH - J 3x1.5mm² The cable for the luminaires will be partially routed in a suspended ceiling and cable trays, and partially in walls under plaster. Cables to the switches will be routed in walls under plaster using appropriate plastic flexible conduits. The price is per linear meter and includes the cable, flexible conduit, auxiliary installation material, and electrical connection on both ends. | m | 2000 | 0 | 0
2.2 | Procurement, delivery and installation of LED linear luminaire, 47.4W, 8020lm, 4000K, IP66. On the floor plan marked as A. Paid per unit. | piece | 13 | 0 | 0
2.3 | Procurement, delivery, and installation of a surface-mounted circular LED luminaire, 19W, 2000lm, 4000K. On the floor plan marked as B (Б). Payment per unit. | piece | 6 | 0 | 0
2.4 | Procurement, delivery, and installation of a surface-mounted circular LED luminaire, 12W, 1250lm, 4000K, IP65. On the floor plan marked as V(В). Payment per unit. | piece | 1 | 0 | 0
2.5 | Procurement, delivery, and installation of recessed circular LED luminaire, 15.2W, 2000lm, 4000K. Payment per unit. | piece | 106 | 0 | 0
2.6 | Procurement, delivery, and installation of ceiling LED luminaire with built-in sensor, MAUVE. On base marked as D (Д). Payment per unit. | piece | 18 | 0 | 0
2.7 | Procurement, delivery, and installation of LED surface-mounted panel 60x60 cm, 34W, 4100 lm, 4000K. On base marked as Ѓ. Payment per unit. | piece | 19 | 0 | 0
2.8 | Procurement, delivery, and installation of LED suspended linear luminaire, length 1690 mm, 63 W, 5900 lm. On base marked as E. Payment per unit. | piece | 5 | 0 | 0
2.9 | Procurement, delivery, and installation of LED suspended linear light fixture, length 1410 mm, 57 W, 5080 lm. On base marked with “Ж”. Payment per piece. | piece | 2 | 0 | 0
2.1 | Procurement, delivery, and installation of LED surface-mounted luminaire with IP44 protection rating, 18 W, 2400 lm. Payment per unit. | piece | 6 | 0 | 0
2.11 | Procurement, delivery, and installation of an LED surface-mounted circular light fixture, 13W, 950 lumens, 4000K. On floor base marked with “Ѕ”. Payment per piece. | piece | 38 | 0 | 0
2.12 | Procurement, delivery, and installation of LED strip 7W/m for under-cabinet kitchen installation, 24V. On base marked with “И”. Payment per piece. | m | 4 | 0 | 0
2.13 | Procurement, delivery, and installation of a standard modular wall switch, complete with box, mounting plate, and cover from a reputable manufacturer. Payment per unit, including electrical connection. | piece | 10 | 0 | 0
2.14 | Supply, delivery, and installation of a serial modular switch for wall mounting, complete with junction box, mounting plate, and cover plate from a reputable manufacturer. Payment is made per unit, including electrical connection. | piece | 6 | 0 | 0
2.15 | Supply, delivery, and installation of alternating modular wall switch, complete with junction box, mounting plate, and cover from a reputable manufacturer. Payment per piece including electrical connection. | piece | 13 | 0 | 0
2.16 | Supply, delivery, and installation of cross modular wall switch, complete with junction box, mounting plate, and cover from a reputable manufacturer. Payment per piece including electrical connection | piece | 1 | 0 | 0
2.17 | Supply, delivery, and installation of push button switch for wall, 10A, 220V, complete with junction box, mounting plate, and cover from a reputable manufacturer. Payment per piece including electrical connection | piece | 21 | 0 | 0
2.18 | Supply, delivery, and installation of modular switch packs for flush wall mounting, 3 modules. Complete with junction box, mounting plate, and cover consisting of: -three standard switches 10A | piece | 3 | 0 | 0
2.19 | Supply, delivery, and installation of modular switch packs for flush wall mounting, 3 modules. Complete with junction box, mounting plate, and cover consisting of: -two alternating switches 10A | piece | 12 | 0 | 0
2.2 | Supply, delivery, and installation of modular switch packs for flush wall mounting, 3 modules. Complete with junction box, mounting plate, and cover consisting of: -three alternating switches 10A | piece | 2 | 0 | 0
2.21 | Supply, delivery, and installation of modular switch packs for flush mounting in wall, 5M. Complete with junction box, mounting plate, and cover plate consisting of: -one single-pole switch 10A -one standard switch 10A -three push buttons 10A | piece | 1 | 0 | 0
2.22 | Supply, delivery, and installation of modular switch packs for flush wall mounting, 5 modules. Complete with junktion box, mounting plate, and cover plate, consisting of: -one single-pole switch 10A -one ordinary switch 10A -three push buttons 10A | piece | 2 | 0 | 0
2.23 | Supply, delivery, and installation of modular push buttons for flush mounting in the wall, 4 modules. Complete with junktion box, mounting plate, and cover plate, consisting of: Four push buttons, 10A each | piece | 1 | 0 | 0
2.24 | Supply, delivery, and installation of a motion detector with the following characteristics: Operating voltage 110 V AC - 230 V AC Frequency 50 - 60 Hz | piece | 4 | 0 | 0
2.25 | "Preparation of a photometric calculation in accordance with the photometric calculation in the project documentation and the offered luminaires. The photometric calculation must demonstrate that the offered luminaires provide a level of illumination that meets the requirements according to the EN 12464-1 standard. The photometric calculation must be completed within 5 working days from the signing of the Contract." | lump sum | 1 | 0 | 0
2.26 | Testing of the installation, commissioning, and issuance of attestations and certificates from reputable manufacturers. A lump-sum payment applies. | lump sum | 1 | 0 | 0
2.27 | Measurement of the illumination intensity in the rooms of the building. Measurements to be performed by an authorized organization accredited by the Ministry of Economy of the Republic of North Macedonia. Payment is lump sum. | lump sum | 1 | 0 | 0
| Total: |  |  |  | 0
3 | ELECTRICAL INSTALLATIONS FOR SOCKETS AND TECHNOLOGICAL CONNECTIONS
3.1 | Procurement, delivery, and installation of conductor type NHXMH-J 3x2.5 mm² for the construction of connection points for single-phase sockets. The conductor will be routed on cable clamps. Payment is made as a complete package including accompanying auxiliary installation equipment, as well as electrical connection at both ends. | m | 1800 | 0 | 0
3.2 | Procurement, delivery, and laying of conductor type NHXMH-J 5x10mm for the installation of connection points for VRF systems. The conductor will be routed partially inside walls under plaster and partially on the ceiling. Payment covers the complete package including accompanying auxiliary installation equipment, as well as electrical connections at both ends. | m | 40 | 0 | 0
3.3 | Procurement, delivery, and laying of conductors type N2XH-O 4x95mm² and N2XH-J 1x50mm for the installation of connection points for a heat pump. The conductors will be routed partially inside walls under plaster and partially on the ceiling. Payment covers the complete package including accompanying auxiliary installation equipment, as well as electrical connections at both ends. | m | 40 | 0 | 0
3.4 | Procurement, delivery, and laying of conductor type NHXMH-J FE180E90 3x2.5 mm² for powering low voltage equipment, fire alarm control panel. The conductor will be routed partially on ceiling cable trays and partially inside walls under plaster in appropriate flexible conduit. Payment includes the complete package with flexible conduit and other auxiliary installation equipment, as well as electrical connections at both ends. | m | 50 | 0 | 0
3.5 | Procurement, delivery, and execution of electrical installation with conductors type H07ZZ-F 4x35mm² and H07ZZ-F 1x16mm². The installation will be routed inside walls under plaster. Payment covers the complete package required for installation including auxiliary installation equipment. (Installation in kitchen) Electrical connections are included in the price. | m | 30 | 0 | 0
3.6 | Procurement, delivery, and execution of electrical installation with conductor type H07ZZ-F 5x10mm². The installation will be routed inside walls under plaster. Payment covers the complete package required for installation, including auxiliary installation equipment. (Installation in kitchen) Electrical connections are included in the price. | m | 45 | 0 | 0
3.7 | Procurement, delivery, and execution of electrical installation with conductor type H07ZZ-F 5x6mm². The installation will be routed inside walls under plaster. Payment covers the complete package required for installation, including auxiliary installation equipment. (Installation in kitchen) Electrical connections are included in the price. | m | 45 | 0 | 0
3.8 | Procurement and wall mounting of an IP54-rated 63A, 3-pole (1-0) ridged switch, surface-mounted, for kitchen. | piece | 2 | 0 | 0
3.9 | Procurement and wall mounting of an IP54-rated 40A, 3-pole (1-0) ridged switch, surface-mounted, for kitchen. | piece | 3 | 0 | 0
3.1 | Procurement and wall mounting of an IP54-rated 25A, 3-pole (1-0) ridged switch, surface-mounted, for kitchen. | piece | 3 | 0 | 0
3.11 | Procurement, delivery, and wall mounting of standard single-phase socket outlet 10/16A 220V. | piece | 38 | 0 | 0
3.12 | Procurement, delivery, and wall mounting of double single-phase socket outlet 10/16A 220V. | piece | 35 | 0 | 0
3.13 | Procurement, delivery, and wall mounting of OG single-phase socket outlet 16A 220V. | piece | 17 | 0 | 0
3.14 | Procurement, delivery, and wall mounting of a 5-module socket outlet package for installation in wall, complete with installation box and frame, on base marked "A", consisting of: two standard single-phase sockets, 250V, 50Hz and one RJ45 socket outlet | piece | 12 | 0 | 0
3.15 | Procurement, delivery, and wall mounting of a 6+2 module socket outlet package for installation in wall, complete with installation box and frame, on base marked "Б", consisting of: -three Schuko single-phase sockets, 250V, 50Hz and two RJ45 socket outlets | piece | 3 | 0 | 0
3.16 | Procurement, delivery, and wall mounting of a 3-module socket outlet package for installation in wall, complete with installation box and frame, on base marked "В", consisting of: -one standard single-phase socket, 250V, 50Hz and one RJ45 socket outlet** | piece | 8 | 0 | 0
3.17 | Procurement, delivery, and wall mounting of a 6-module socket outlet package for installation in wall, complete with installation box and frame, on base marked "E", consisting of: two standard single-phase sockets, 250V, 50Hz and two RJ45 socket outlets | piece | 1 | 0 | 0
3.18 | Floor box with dimensions 281x281x65mm, with a cover for 12 modules, with built-in components, on base marked "G": 8 x standard single-phase sockets 220V, 16A 4 x RJ45 sockets | piece | 3 | 0 | 0
3.19 | Floor box with dimensions 281x191x65mm, with a cover for 10 modules, with built-in components, on base marked "Д": 4 x standard single-phase sockets 220V, 16A 2 x RJ45 sockets | piece | 2 | 0 | 0
3.2 | Thermoplastic conduit, CS 25m | m | 30 | 0 | 0
3.21 | Thermoplastic conduit, CS 32m | m | 30 | 0 | 0
3.22 | Procurement, delivery, and wall mounting along the evacuation route of a metal cabinet with built-in buttons for remote disconnection of the main switch in the Main Distribution Board, with a glass door and a sign reading "In case of fire, break glass and switch off", complete with electrical connection. | piece | 2 | 0 | 0
3.23 | Procurement, transport, and laying of cable inside the wall under plaster in appropriate flexible conduit, type: NHMH 3x1.5mm², for buttons used for AC switch disconnection. | m | 5 | 0 | 0
3.24 | Testing of the installation, issuance of a certificate, and commissioning by an authorized organization accredited by the Ministry of Economy of the Republic of North Macedonia. Paid as a lump sum. | lump sum | 1 | 0 | 0
| Вкупно: |  |  |  | 0
4 | EMERGENCY LIGHTING INSTALLATIONS
4.1 | Procurement, delivery, and installation of conductors for connection points for panic lights of the type: NHXMH - J 3x1.5mm² The cable will be routed partially on the ceiling under plaster, fastened to a solid structure with halogen-free clamps and other accompanying installation materials, and partially routed inside the wall under plaster within appropriate flexible plastic conduit. Payment is per meter for the complete set including cable, flexible conduit, and other auxiliary installation materials, along with electrical connection at both ends. | m | 300 | 0 | 0
4.2 | Procurement, delivery, and installation of an “EXIT” panic light with its own power source, rechargeable battery with 90 minutes autonomy, marked with "E". Payment is per unit. | piece | 16 | 0 | 0
4.3 | Procurement, delivery, and installation of a “directional arrow” panic light with its own power source, rechargeable battery with 90 minutes autonomy, marked with "E1". Payment is per unit. | piece | 17 | 0 | 0
4.4 | Testing of the panic lighting installation, issuance of certification, and commissioning. Payment is lump sum for the complete scope. | lump sum | 1 | 0 | 0
| Total: |  |  |  | 0
5 | CABLE TRAYS
5.1 | Procurement, delivery, and installation of a cable tray (PNK rack) made of perforated hot-dip galvanized steel sheet according to DIN EN ISO 1461, with a width of 200 mm and length of 3 m The position includes: Quality material for safe cable support and installation. Perforated trays with quick coupling. Brackets made of hot-dip galvanized steel sheet with screws for fastening. US3 crossed supports. -90º bends. -Angle joint and built-in "T" connector. -Additional supports placed 20 cm before and after every bend or "T" joint. -Phase elements made of hot-dip galvanized steel sheet with appropriate covers. -Threaded connector, longitudinal dividing element. -Anchors and turret screws. All necessary small mounting materials for complete installation. Payment is per piece. | piece | 38 | 0 | 0
| Total: |  |  |  | 0
Low-voltage installations
6 | Automatic Fire Alarm System
Equipment and Materials
6.1 | Analog Addressable Fire Alarm Control Panel with One Loop -Single loop supporting up to 240 addresses -Automatic device addressing capability on the loop -Auto-switching between two modes (day/night) -Automatic detector testing functionality -Network capability for up to 48 panels in a "token-ring" fault-tolerant topology -TCP/IP networking support for up to 20 panel clusters -Optional integrated PSTN / 3G / GSM communicator for event reporting -LAN network connection capability -LCD display with function keys and status LEDs -Event signaling and emergency calling capability even in case of main processor failure -Includes 1.5A power supply and battery charger -USB port for configuration -Micro SD card slot for configuration data storage/loading -Protocol: Enea -Certifications: CPR EN54-2, EN54-4, EN54-13, EN54-21 (for all communication channels), EN12094-1 (extinguishing) -MANUFACTURER: Inim -TYPE: S-PREVIDIA-C100LG | piece | 1 | 0 | 0
6.2 | Battery 12V, 7Ah -Initial charging current not exceeding 2.1 A -Sealed, maintenance-free design MANUFACTURER: Ultracell TYPE: ULTRA1270 | piece | 2 | 0 | 0
6.3 | Analogue Addressable Optical Smoke Fire Detector with Built-in Short-Circuit -Isolator, Enea Protocol -Mandatory automatic addressing by the fire alarm control panel -Mandatory manual addressing option via the control panel -Mandatory adjustable detector sensitivity with separate settings for day and night modes Built-in short-circuit isolator -Advanced optical chamber design with a fine mesh (500 μm holes) to prevent insect entry, enhancing false alarm immunity -Tri-color LED with 360° visibility -Remote configuration of sensitivity and operating mode via EDRV1000 driver and software MANUFACTURER: Inim TYPE: S-ED100 | piece | 51 | 0 | 0
6.4 | Analogue Addressable Heat Fire Detector with Built-In Short-Circuit Isolator, Enea Protocol -Mandatory automatic addressing by the fire alarm control panel -Mandatory manual addressing option via the fire alarm control panel -Mandatory adjustable sensitivity of detectors with separate settings for day and night modes -Built-in short-circuit isolator -Selectable heat detection modes: fixed temperature threshold (two threshold levels) and/or rate-of-rise detection -Tri-color LED with 360° visibility -Remote configuration of sensitivity and operating mode via driver and software MANUFACTURER: Inim TYPE: S-ED200 | piece | 6 | 0 | 0
6.5 | Base for Fire Detector -Includes a contact plate (bridge) that ensures loop continuity in the event of detector removal MANUFACTURER: Inim TYPE: S-EB0010 | piece | 57 | 0 | 0
6.6 | Addressable Manual Call Point with Built-in Short Circuit Isolator, Resettable Element with Plastic Key, Red Color, Inim Protocol -Warning flag and LED confirmation of activation -Resettable element with plastic key (included in the kit) -Ability to check the status of the call point from the control panel -Reusable multiple times, no need to break glass -Built-in short circuit isolator Manufacturer: Inim Type: S-EC0020 | piece | 8 | 0 | 0
6.7 | Input/Output Module with Built-in Short Circuit Isolator -1 supervised input -1 supervised voltage output -1 relay potential-free output Manufacturer: Inim Type: S-EM312SR | piece | 6 | 0 | 0
6.8 | Surface Mount Junction Box for Inim Control Modules, dimensions 100 x 100 x 50 mm Manufacturer: (generic) Type: (generic) | piece | 6 | 0 | 0
6.9 | Addressable Fire Alarm Sounder with Built-in Short Circuit Isolator -Powered with the loop or external power supply -Thermoplastic housing, red color -Selection of 14 tones -Synchronization capability with other sounders in the system -LED signal indication -Sound pressure up to 101dB(A) @1m -Built-in short circuit isolator (according to EN54-17) -Protocol: Inim -Power supply: 18–30V DC -Standby current: 200μA -Alarm current: 1.4–20mA (depending on the operating mode) -Protection: IP65 (IP21 compliant with EN54-3), suitable for outdoor mounting -Operating temperature: -20°C to +70°C MANUFACTURER: Inim TYPE: S-ES2011RE | piece | 3 | 0 | 0
6.1 | Addressable fire alarm siren with strobe light and built-in short circuit isolator, Inim protocol Powered from the loop or external power supply Thermoplastic red housing Selection of 14 tones and 2 brightness levels (via EITK2000 or Previdia control panels) Synchronization capability with other sirens in the system LED signaling with color change option Sound level up to 101dB(A) @ 1m Integrated short circuit isolator (according to EN54-17) Enea protocol Strobe light color: white Power supply: 18-30 Vdc Quiescent current: 200μA Alarm current: 10-40mA (depending on operating mode) IP65 protection, suitable for outdoor installation (IP21 compliant with EN54-3) Operating temperature: -20°C to +70°C Manufacturer: Inim Model: S-ES2020RE | piece | 2 | 0 | 0
6.11 | Minor unspecified consumable material wall plugs, screws, zip ties, installation rods, gypsum, patch cables, etc. MANUFACTURER: Generic MODEL/TYPE: Generic | lump sum | 1 | 0 | 0
6.12 | Logbook for Regular Inspections of the Fire Protection System MANUFACTURER: Alarm automatika TYPE: KO 2-DP | lump sum | 1 | 0 | 0
6.13 | Fire-resistant cable, JEB-H(St)H FE180 E30-E90 2x2x0.8 Halogen-free cable for fire alarm installations with electrostatic shielding aluminum foil, enhanced fire performance ensuring electrical conductivity is maintained between 30 and 90 minutes, red color MANUFACTURER: Generic TYPE: JEB-H(St)H FE180 E30-E90 1x2x0.8 | m | 200 | 0 | 0
6.14 | Fire Alarm Cable J-H(St)H 2x2x0.8mm MANUFACTURER: (generic) TYPE: J-H(St)H 2x2x0.8mm | m | 500 | 0 | 0
6.15 | Supply, delivery, and installation of a 24V / 5.2A power supply (4A + 1.2A for battery charging), housed in a metal cabinet with dimensions 497 x 380 x 87 mm. Capable of accommodating 2 rechargeable 7Ah batteries. At least 3 separate voltage outputs. Four functional control buttons. One output relay for fault indication. LED status signaling. Mandatory protection against overload and short circuit. Capability to connect a monitoring loop for power supply status and output supervision. Installed flush-mounted into new partition walls, below ceiling height (if necessary, additional drywall finishing to ensure the cabinet does not protrude beyond the wall surface). For electromagnetic door holders (door holders)... Payment is per unit. | piece | 4 | 0 | 0
6.16 | Supply, delivery, and installation of backup batteries for a power unit, 12V, 7 Ah. Payment is per unit. | piece | 4 | 0 | 0
6.17 | Supply, delivery, and installation of a surface-mounted enclosure for input/output modules with IP55 protection rating. Payment is per unit. | piece | 6 | 0 | 0
6.18 | Magnetic door holder for fire protection (normally open) doors, suitable for universal mounting on wall or floor, with a manual release button. Complete with counter metal bracket. Holding force: 800 N. 24 V DC (for each fire protection door leaf separately). | piece | 4 | 0 | 0
6.19 | Installation of addressable fire alarm control panel: -Wall mounting of the addressable control panel using appropriate anchors and screws, and pulling the cables from the fire alarm installation into the panel -Installation and connection of the batteries for the fire alarm control panel -Stripping the cable insulation and neat routing and connection inside the control panel | piece | 1 | 0 | 0
6.2 | Installation of a base for a fire detector and connection of the loop. | piece | 57 | 0 | 0
6.21 | Mounting the fire detector on the base and addressing it. | piece | 57 | 0 | 0
6.22 | Installation and connection of a manual fire detector and addressing | piece | 8 | 0 | 0
6.23 | Installation and connection of an indoor fire alarm siren and addressing. | piece | 3 | 0 | 0
6.24 | Installation and connection of an outdoor fire alarm siren with anchors and screws | piece | 2 | 0 | 0
6.25 | Installation of an input/output module. | piece | 6 | 0 | 0
6.26 | Procurement and installation of all necessary signs and labeling of all fire protection system elements according to the project. | piece | 76 | 0 | 0
6.27 | Programming of the addressable fire alarm control panel By address (detector, manual call point, siren, module, etc.) | piece | 1 | 0 | 0
6.28 | Drilling a hole in the wall with a diameter of Ø 24 mm Through walls up to 300 mm thick | piece | 1 | 0 | 0
6.29 | Connection of the fire alarm control panel to the power supply Installation of the main power supply cable from the network, 3x1.5 mm² (approx. 20m) to the fuse cabinet, and connection of the fuse in the distribution board. | lump sum | 1 | 0 | 0
6.3 | Laying the cable mainly along the ceiling, including procurement and installation of PNT conduits and other necessary installation materials. | m | 700 | 0 | 0
6.31 | Issuance of a certificate of functionality for the fire protection system. | lump sum | 1 | 0 | 0
6.32 | Training for operation of the fire protection system. | lump sum | 1 | 0 | 0
| Total: |  |  |  | 0
7 | VIDEO SURVEILLANCE INSTALLATIONS
7.1 | Supply, delivery, and installation of a minimum 16-port PoE switch -16 PoE ports + 2 SFP ports -16 x 10/100 Base-T (PoE powered) -Total PoE budget: 250W -Rack mountable Compliant with the Restriction of Hazardous Substances (RoHS) directive. | piece | 1 | 0 | 0
7,2 | Delivery and installation of IR Outdoor 6MP Dual Illumination IP Video Camera -Compliant with NDAA standards -Resolution: 6MP@20fps / 4MP, 2MP@25fps -Fixed lens: 2.8mm -2 x Array Black Glass IR LEDs with range 30–50m -White Light LED with range 30–50m for full-color night vision -Optical sensor: 1/2.7'' SmartSens SC530A -Day/Night function: ICR -Minimum illumination: 0.0085 lux @ F1.2 -Dynamic range: True WDR 120 dB -Built-in advanced AI video analytics with human and vehicle detection and recognition -1 audio input, 1 built-in microphone -SD card slot for onboard memory -ONVIF protocol support -H.265+ compression -Protection rating: IP67-Power supply: 12V DC / PoE | piece | 7 | 0 | 0
7.3 | Delivery and installation of Dome 6MP Dual Illumination IP Video Camera -Compliant with NDAA standards -Resolution: 6MP@20fps / 4MP, 2MP@25fps -Fixed lens: 2.8mm -2 x Array Black Glass IR LEDs with range 20–30m -White Light LEDs with range 20–30m for full-color night vision -Optical sensor: 1/2.7'' SmartSens SC530A -Day/Night function: ICR -Minimum illumination: 0.0085 lux @ F1.2 -Dynamic range: True WDR 120 dB -Built-in advanced AI video analytics with human and vehicle detection and recognition -1 audio input, 1 built-in microphone -SD card slot for onboard memory -ONVIF protocol support -H.265+ compression -Protection rating: IP67 -Power supply: 12V DC / PoE -Warranty: 3 years | piece | 3 | 0 | 0
7,4 | Supply and installation of a junction box for DVC cameras Dimensions: 110 x 40 mm | piece | 10 | 0 | 0
7.5 | Supply and installation of a standalone 16-channel real-time NVR (Network Video Recorder) -Compliant with NDAA standards -Supports resolutions: 12MP / 8MP / 6MP / 5MP / 4MP / 3MP / 1080p @ 25fps -Real-time recording: 25fps per channel -Input bandwidth: 160 Mbps -Compression: H.265s / H.265+ / H.265 / H.264 -Supports 2 x SATA HDD up to 10TB -Network interface: 1 x Gigabit LAN port -Video outputs: HDMI 2K/4K and VGA -ONVIF protocol supported -Supported features: DHCP, P2P, auto DDNS, web server, mobile client, dual stream, audio -RS485 interface -Power supply: DC 12V 4A (included in the package) -Warranty: 3 years | piece | 1 | 0 | 0
7.6 | Server for installation of software for security systems integration, with the following minimum configuration: -Processor: Minimum 6-core CPU, 3.4GHz, 12MB Cache -Maximum power consumption of the CPU: 80W -RAM: Minimum 32GB -Storage: -Minimum 2 x 480GB SSD Mixed Use (or equivalent) -Minimum 2 x 1TB HDD Mixed Use (or equivalent) -Drives labeled as READ Intensive will not be accepted -Disk controller: Minimum RAID 10 controller -Network connectivity: 2 x 1Gbit network ports, RJ45 -Power supply: Minimum 500W -Peripherals: -Wired keyboard from the same manufacturer as the server -Optical mouse from the same manufacturer as the server -Chassis: Maximum 1U Rack Mount format -Operating system: Windows Server 2019 -Other requirements: -Rack mounting rails must be delivered with the server All server components must be from the same manufacturer as the server Manufacturer: Generic Model: Generic | piece | 1 | 0 | 0
7.7 | LED Monitor 43" -24/7 operation -4K resolution -With 1 DisplayPort, 2 HDMI, 1 VGA, and 1 x RS232 (in/out) -Video standard: PAL, NTSC -Brightness: 450 cd/m², Contrast Ratio: 3000:1 -Number of Colours: 1.07 billion -Response Time: 5 ms -Speakers: 2 x 5 W -Includes wall mount, HDMI cable, and remote control -MTBF at 25°C: > 50,000 hours -Operating temperature: 0°C ~ +40°C, Humidity: < 90% -Manufacturer: (generic) -Model/Type: (generic) | piece | 2 | 0 | 0
7,8 | Procurement, transport, and laying of cable for CCTV installation (in accordance with standards EN 50173; EN 50288; IEC 60332-1; IEC 61156-5; ISO/IEC 11801); type: F/UTP FTP 4x2x0.51mm, Cat6. The cable shall be routed along the wall in appropriate plastic flexible conduit. Payment is per linear meter, including auxiliary materials and electrical connection at both ends. | m | 300 | 0 | 0
7,9 | Delivery and installation of an RJ45 network connector, min. Cat 6a. | piece | 20 | 0 | 0
7,10 | Inspection of the entire system, configuration, functional testing, and official commissioning of the system Installation testing and issuance of a certificate by an authorized company. Training of the end user's employees for operation of the complete system according to the supplier's recommendations. | lump sum | 1 | 0 | 0
7,11 | Training of the employee staff for handling the complete system according to the manufacturer's recommendations (5 persons). | lump sum | 1 | 0 | 0
7,12 | Testing of the system functionality and installation by an authorized organization, with issuance of certificate and attestation. | lump sum | 1 | 0 | 0
| Total: |  |  |  | 0
8 | INSTALLATION FOR STRUCTURED CABLING (Internet and Telephone Installation)
NOTE: Modular outlets that serve as connection points for internet, TV, or telephony are included in the bill of quantities under chapter I4 "ELECTRICAL INSTALLATIONS FOR OUTLETS."
8.1 | Delivery and installation of a RACK cabinet with a minimum size of 24U, dimensions H=1.21m, W=0.65m, D=0.6m; equipped with the following components: -1x minimum 24-port full patch panel with built-in modules of at least Cat.6a -1x standard socket for power supply from a backup power distribution board -1x power strip with at least 6 outlets, 6x 2P+E, 1U -1x fan unit with at least 2 fan elements -4x cable organizers for rack cabinets -Required number of patch cords corresponding to the number of units connected to the rack -Required number of connectors for the cables terminating in the RACK cabinet -The dimensions of the rack must match the equipment installed inside | piece | 2 | 0 | 0
8.2 | Procurement, transport, and installation of a managed switch with 48 independent ports including a combo group, 1U rack-mountable or wall-mountable, featuring 48 × RJ-45 10/100/1000 Mbps ports, 4 × SFP 100 Mbps/1 Gbps slots, operating at 100–240 VAC, 50/60 Hz, 2.0 A. The device must comply with the "Restriction of Hazardous Substances (RoHS)" directive. | piece | 4 | 0 | 0
8.3 | Procurement, transport, and installation of a CCO (Cabinet for Multimedia and Communication Devices), made of polyester for wall mounting. It should allow for telephone connections, installation of modems and routers, and connection to cable operators. The cabinet must include a perforated mounting plate with built-in equipment: One socket for DIN rail mounting, 16A, 1 pole Quantity: 1 unit | piece | 6 | 0 | 0
8.4 | Procurement, transport, and installation of cable for structured cabling installation (according to standards EN 50173; EN 50288; IEC 60332-1; IEC 61156-5; ISO/IEC 11801;) type: F/UTP Cat 6A 4x2x0.51mm LSZH. The cable will be routed partially in a suspended ceiling, partially inside the wall to connection points where it must be laid in halogen-free conduit, and partially in the floor in appropriate flexible conduit. Payment is per meter of installed cable complete with halogen-free conduit and other auxiliary installation materials, including electrical termination at both ends. | m | 1800 | 0 | 0
8.5 | Labelling of cables with permanent tags on both ends. | lump sum | 1 | 0 | 0
8.6 | Thermoplastic conduit, Ø50mm, for operator entry into the building. | m | 30 | 0 | 0
8.7 | Control of the entire system, measurements, functional testing of the system, and official commissioning of the system. Training of the user's staff for operating the complete system according to the supplier's recommendations. | lump sum | 1 | 0 | 0
| Total: |  |  |  | 0
9 | INSTALLATION FOR ACCESS CONTROL
Equipment and Materials
9.1 | Software for Working Time Recording (WTR) and Access Control -Web-based application -Includes SQLite database -In Macedonian language with Cyrillic script, compliant with legal regulations for WTR -Unlimited number of controllers and users -Supports various groups and intervals for access control and WTR (fixed, flexible, and shift work schedules) -Customizable reports -Capability for automatic report generation -Expandable with additional modules -Must be from the same manufacturer as the Working Time Recording equipment Manufacturer: Jantar Model: JAN CODEKS TA V10 | piece | 1 | 0 | 0
9.2 | Access Control Controller for 2+1 Doors -Memory for 30,000 users, expandable up to 100,000 users -Memory for 100,000 events -Supports 3PRO protocol readers -Capability to connect up to 6 readers -Integrated 40W power supply module -Plastic enclosure with IP21 protection, dimensions 180 x 180 x 80 mm -2 x RS485 and TCP/IP communication interfaces -Can also be used as an RS485/TCP/IP communication converter -3 relay outputs - 0.5A each -Battery backup slot -Operating temperature: -20 °C to 70 °C Manufacturer: Jantar Model: JAN POPULUS P-2-S | piece | 1 | 0 | 0
9.3 | Time Attendance Terminal -4.3" touch-sensitive LCD screen -Built-in reader for contactless MIFARE cards/tags at 13.56 MHz -Memory for 500 / 30,000 users and 100,000 events -3PRO Ready protocol -Communication via RS485 and TCP/IP -Voltage output for lock control -Inputs for magnetic contact and exit button Manufacturer: Jantar Model: JAN REGIS H-3-B | piece | 1 | 0 | 0
9.4 | Touch-sensitive Exit Button -Stainless steel housing -Color in inactive mode: blue, color when activated: green -NC/NO contacts -EXIT icon -Manufacturer: S-Link Model: SL-EXIT1 | piece | 2 | 0 | 0
9.5 | Contactless Mifare Reader - 13.56MHz RFID Cards with Built-in 3PRO Protocol -Reading frequency: 13.56MHz -3PRO ready (supports 3PRO cards and 3PRO communication with controller) -IP65 protection rating -Reading distance up to 7 cm -Audible and visual LED indication -Housing type O - without keypad Manufacturer: Jantar Model: JAN READER O-3-S | piece | 2 | 0 | 0
9.6 | Electric Lock 12/24V DC -Fail-safe (opens when no power) -Power consumption: 200mA @12V / 100mA @24V -Holding force: 5,000 N -Symmetrical design with universal mounting for both left and right-opening doors Manufacturer: Geze Model: GEZE A5300-B | piece | 2 | 0 | 0
9.7 | RFID Contactless ISO Card with Encryption -Reading frequency: 13.56 MHz -Mifare Desfire protocol -Contains standard UID -Encrypted encoding (3PRO Ready) Manufacturer: Jantar Model: JAN CARD C-3-D (C-3-M) | piece | 100 | 0 | 0
9.8 | Battery 12V, 2.4Ah -Current before first use not higher than 0.72 A -Sealed, maintenance-free Manufacturer: Ultracell Model: ULTRA1219 | piece | 1 | 0 | 0
9.9 | Server for Installation of Software for Integration of Security Systems, with the Following Minimum Configuration: -Processor: Minimum CPU: 6 cores, 3.4 GHz, 12MB Cache -Maximum: 80W CPU power consumption -RAM Memory: Minimum 32GB -Hard Drives: Minimum 2 x 480GB SSD Mixed Use or equivalent -Minimum 2 x 1TB HDD Mixed Use or equivalent -Disks marked as READ Intensive will not be accepted -Disk Controller: min. RAID 10 controller -Network Connectivity: 2x 1Gbit network, RJ45 -Power Supply: min. 500W -Keyboard and Mouse: Minimum wired keyboard from the same manufacturer -Minimum optical mouse from the same manufacturer -Chassis Format: max. 1U Rack Mount -Operating System: Windows Server 2019 Other Features: Mounting rails to be delivered with the server Components inside the server must be from the same manufacturer as the server Manufacturer: (generic) Model: (generic) | piece | 1 | 0 | 0
9.1 | Network LAN Cable with 4 pairs, Category 6 (Cat.6) S/UTP type -With separate insulation of aluminum foil -With combined insulation Manufacturer: (generic) Model: UTP Cat6 | m | 30 | 0 | 0
9.11 | Flexible Cable 3 x 0.75 mm², white color | m | 20 | 0 | 0
Works and Services
9.12 | Installation, connection, and configuration of door controllers and power supply modules Installation and connection of power supply modules and batteries. | piece | 1 | 0 | 0
9.13 | Installation, connection, and configuration of card readers. | piece | 2 | 0 | 0
9.14 | Installation, connection, and configuration of card readers. | piece | 2 | 0 | 0
9.15 | Installation, connection, and programming of the Time Attendance terminal. | piece | 1 | 0 | 0
9.16 | Installation and connection of electric locks in pre-prepared doors (factory-made installation openings). | piece | 2 | 0 | 0
9.17 | Laying 3x0.75 cable in installation conduits and channels. | m | 20 | 0 | 0
9.18 | Laying UTP cable in installation conduits and channels | m | 30 | 0 | 0
9.19 | Installation, configuration, and programming of the access control server -Installation of necessary software on the server -Registration and configuration of controllers, power modules, and readers -Setting access rights -Registering users into categories -Defining reports | piece | 1 | 0 | 0
9.2 | Installation, configuration, and programming of the Time Attendance (TA) server -Installation of necessary software on the server -Registration and configuration of controllers -Setting time schedules -Registering users into groups -Defining reports | piece | 1 | 0 | 0
9.21 | Training on operation of the access control and time attendance system. | lump sum | 1 | 0 | 0
| Total: |  |  |  | 0
10 | EQUALIZATION POTENTIAL INSTALLATIONS
10,1 | Procurement, delivery, and installation of a wall in technical and machine rooms, a potential equalization busbar with twelve terminals installed in a metal enclosure with dimensions (450x150x50) mm. Payment is made for the complete set as per the specified quantity. | piece | 2 | 0 | 0
10,2 | Procurement, delivery, and laying of galvanized steel strip FeZn 25x4mm from EPS to the telemeter ground. Payment is made per complete set per linear meter required. | m | 15 | 0 | 0
10,3 | Procurement, delivery, and installation of a wall in front of the bathroom for potential equalization, art. 1981, up to a height of h=0.6m from the finished floor. Payment is made for the complete set per unit. | piece | 4 | 0 | 0
10,4 | Procurement, delivery, and laying of conductor type NYY-J-1x35mm² for interconnection between potential equalization boxes. The cable will be routed partially on the wall under plaster and partially through PVC channels. Payment is made for the complete set per unit. | m | 30 | 0 | 0
10,5 | Procurement, delivery, and laying of conductor type NYY-J-1x16mm² for connecting the potential equalization busbars with the potential equalization boxes. The cable will be routed partially on the wall under plaster and partially through PVC channels. Payment is made for the complete set per unit. | m | 60 | 0 | 0
10,6 | Procurement, delivery, and laying of conductor type NYY-J-1x16mm² from the potential equalization box to all metal parts in bathrooms and sanitary facilities (metal pipes, bathtub, drain). The cable will be routed on the wall under plaster. The average cable length per connection is 5 meters. Payment is made for the complete set per unit. | m | 40 | 0 | 0
10,8 | Testing of the potential equalization installation, commissioning, and issuing of a certificate by an authorized organization accredited by the Ministry of Economy of the Republic of North Macedonia. Payment is made as a lump sum. | lump sum | 1 | 0 | 0
| Total: |  |  |  | 0
11 | PUBLIC ADDRESS AND VOICE ALARM SYSTEM
Equipment and Materials
11.1 | 6" – 6W Ceiling Speaker -Outer diameter: 6" -Ceiling-mounted without external frame -With transformer for 100V line -Power: 6W RMS -Frequency response: 140–20,000 Hz -Sensitivity: 92 dB ±3 dB at 1W/1m -Dimensions: 188 mm Ø x 80 mm depth -Cutout diameter: 168 mm Ø MANUFACTURER: Fonestar TYPE: FON GAT-601 | piece | 25 | 0 | 0
11.2 | Bi-directional projection speaker (2x5") -With transformer for 100V line -Power: 20W RMS (30W max) -Frequency response: 180–16,000 Hz -Sensitivity: 86 dB at 1W/1m -Dispersion: 2x170° at 1 kHz, 2x100° at 2 kHz, 2x60° at 4 kHz (-6 dB) -Protection: IP-55 (EN 60529) -Material: ABS enclosure, aluminum mounting bracket and grille, stainless steel screws -Temperature range: -25°C to +55°C -Dimensions: 138 mm Ø x 200 mm depth MANUFACTURER: Fonestar TYPE: FON PF-27TD | piece | 10 | 0 | 0
11.3 | PA amplifier with 4 zones and Bluetooth/USB/FM player -Power: 240W RMS -Outputs: 100V, 4Ω (4 zones with volume control and individual zone on/off) -Inputs: 3 microphone/line inputs with 48V Phantom power, 2 AUX, 1 emergency -Microphone input with mix, gain, and priority level control -Emergency and mute input for connection with alarm or evacuation system -Player: Bluetooth, USB, FM radio -Protections: Against overvoltage, overheating, and short circuit -Temperature range: 0°C to +40°C -Dimensions: 433 x 89 x 360 mm (2U 19" rack) MANUFACTURER: Fonestar TYPE: FON PROX-240Z | piece | 2 | 0 | 0
11.4 | Audio matrix with 8 analog inputs and 8 output zones -4 programmable digital input/output channels -DSP signal processing -Connectivity: PC software, Android and iOS applications, remote controllers -DANTE compatible -Power supply: 100-240 V AC, 80 W MANUFACTURER: Fonestar TYPE: FON MPX-4088 | piece | 1 | 0 | 0
11.5 | Volume and zone selection controller -Volume control and zone selection for the audio matrix -Connection: RJ-45 via Cat 5e cable -Outputs: 2 balanced audio outputs -MANUFACTURER: Fonestar -TYPE: FON MPX-420V | piece | 1 | 0 | 0
11.6 | Microphone with zone selector -Functions: Selection of 1 to 32 zones, broadcasting musical warning tones -Connection: RJ-45 via Cat 5e cable -Inputs: 1 balanced microphone input (XLR 6,800 Ω), 1 mini-USB port for MP3/WAV tones, 1 RD port for connection to the matrix -Power supply: 24 V DC, 100 mA via RD port MANUFACTURER: Fonestar TYPE: FON MPX-400MIC | piece | 1 | 0 | 0
11.7 | Speaker cable 2 x 1.5 mm² | m | 350 | 0 | 0
Works and Services
11.8 | Mounting and connection of amplifiers | piece | 2 | 0 | 0
11.9 | Installation and connection of an audio matrix system complete with microphone and controller | piece | 1 | 0 | 0
11.1 | Installation and connection of speakers | piece | 35 | 0 | 0
11.11 | Laying speaker cables in installation conduits and channels | m | 350 | 0 | 0
1111.11,12 | Training for operating the public address and notification system | lump sum | 1 | 0 | 0
| Total: |  |  |  | 0
12 | LIGHTNING PROTECTION AND PROTECTIVE GROUNDING
12.1 | Delivery and installation of galvanized FeZn tape 30x4mm in foundations for execution of foundation grounding and leads to measuring points, DGRТ. Payment is per linear meter. | m | 240 | 0 | 0
12.2 | Tape splice joint for foundations (90x90) on base labeled as 1. | piece | 25 | 0 | 0
12.3 | Delivery and installation of galvanized FeZn tape 25x4mm on the roof for the execution of lightning protection installations. Payment is per linear meter. | m | 200 | 0 | 0
12.4 | Cross element for tape-tape connection on the roof (60x60), on floor base markes as 3. | piece | 31 | 0 | 0
12.5 | Connection of steel galvanized tape with gutter (connection on the slope of the gutter), on bas floor marked as 4. | piece | 5 | 0 | 0
12.6 | Bracket for steel galvanized tape for guiding the tape along the roof, on base floor marked as 1. | piece | 130 | 0 | 0
12.7 | Bracket for steel galvanized tape for guding the tape along the roof slope on based marked as 2. | piece | 35 | 0 | 0
12.8 | Supply and installation of a measuring junction box MKS.N.V4.912, complete with measuring junction MKS.N.V4.932. Payment is made per complete set including connections. | piece | 6 | 0 | 0
12.9 | Supply and installation of galvanized strip FeZn-30x4mm for execution of leads for combined grounding (to measuring points, DGRТ, diesel generator at the gatehouse, sprinkler station, ramps). Payment is made per running meter complete. | m | 100 | 0 | 0
12.1 | Testing and measurement of grounding resistance complete with certificate from an authorized organization accredited by the Ministry of Economy of the Republic of North Macedonia, inspection of the entire installation, and handover to the investor. | lump sum | 1 | 0 | 0
| Total: |  |  |  | 0
13 | SPRINKLER STATION INSTALLATIONS
13.1 | Surface-mounted metal modular enclosure Prisma G, manufactured from double-decaped sheet metal, electrostatically powder-coated. The enclosure must be type-tested, with Ue 690V, IP54 protection, and dimensions sufficient to ensure proper thermal sizing of the equipment inside, including 20% reserve space. The price shall include copper distribution busbars, terminal blocks, cable glands, busbar holders, conductors, ferrules, cable lugs, permanent outgoing circuit labels, and a single-line diagram in a plasticized cover. The enclosure shall be delivered with a certificate for type-tested panel, electrical equipment, test report, and a manufacturer’s certificate for licensed panel builder. The panel shall be assembled in accordance with the project documentation and include the following equipment:
| - 1 pc changeover switch, 40A, 3-pole, (1-0) -2 pcs miniature circuit breaker B10A, 1-pole -1 pc miniature circuit breaker B16A, 1-pole -1 pc miniature circuit breaker C16A, 3-pole -1 pc miniature circuit breaker C16A, 1-pole - Modular surge arrester with integrated automatic circuit breaker, 3 poles + N, 350V, type T1+T2, with remote transfer - 1 pc single-line diagram in a plastic pocket * 20% spare space * Miscellaneous unspecified small materials | piece | 1 | 0 | 0
13.2 | PVC rigid pipe Ø100 mm, length = 3 m, for building entry | piece | 1 | 0 | 0
13.3 | Procurement and installation of a power supply cable from DGRТ-ADMIN_A to the distribution panel for the sprinkler station DRT-Sprinkler. Fabrication of the complete cable connection with all necessary accessories. Cable type: N2XH-J-5x10mm² (FE180E90). The cable will be routed partially in a trench underground and partially on the wall using cable trays. Payment will be made per linear meter for the complete scope. | m | 40 | 0 | 0
13.4 | Procurement and installation of a power supply cable from DRT-Sprinkler to the pump. Fabrication of the complete cable connection with all necessary accessories. Cable type: N2XH-J-5x6mm² (FE180E90). The cable will be routed on the wall using cable trays. Payment will be made per linear meter for the complete scope. | m | 25 | 0 | 0
13.5 | Procurement and installation of a power supply cable from DRT-Sprinkler to jockey pump. Fabrication of the complete cable connection with all necessary accessories. Cable type: N2XH-J-5x2.5mm² (FE180E90). The cable will be routed on the wall using cable trays. Payment will be made per linear meter for the complete scope. | m | 10 | 0 | 0
13.6 | Procurement, delivery, and installation of conductors for the fabrication of lighting points of the type: NHXMH-J 3x1.5mm² The cable for the luminaires will be routed on cable trays. Payment will be made per linear meter, including the complete cable, flexible conduit, and other auxiliary installation materials, together with the electrical connection at both ends. | m | 20 | 0 | 0
13.7 | Procurement, delivery, and installation of LED surface-mounted waterproof linear luminaire, with a polycarbonate housing, approximately 1200 mm in length. Luminaire power approximately 30W ±10%, luminous flux output approximately 4000 lm ±10%, color temperature 4000K, efficacy 140 lm/W, color rendering index CRI > 80. Mechanical protection rating IP65, IK08. Operating hours 50,000 with luminous flux maintenance above 80%. Operating temperature range from -20°C to +40°C. CE and ENEC quality certificates. Marked as "1" on the basis. Minimum 5-year warranty. Type: WT120C PSU L1200 LED40S/840 Philips. | piece | 3 | 0 | 0
13.8 | Procurement, delivery, and installation of “EXIT” emergency exit sign light for mounting on steel structure, with pictogram, internal power supply, rechargeable battery with 90-minute autonomy. Payment will be made per unit. (Marked as E in the bill of quantities) | piece | 1 | 0 | 0
13.9 | Procurement, delivery, and installation of emergency exit sign light “------->” for mounting on steel structure, with pictogram, internal power supply, rechargeable battery with 90-minute autonomy. Payment will be made per unit. (Marked as E1 in the bill of quantities) | piece | 1 | 0 | 0
13,10 | Procurement, delivery, and installation of a standard OG switch | piece | 1 | 0 | 0
13,11 | If you want, I can help you make it a bit more formal or technical, for example: Procurement, delivery, and installation of a standard OG-type switch for electrical installations. | m | 10 | 0 | 0
13,12 | Procurement, delivery, and installation of conductor type: N2XH-J-3x2.5mm². The conductor will be routed on the wall using cable trays. Payment will be made for the complete scope, including all accompanying auxiliary installation materials, as well as electrical connections at both ends. | m | 10 | 0 | 0
13,13 | Industrial plug package consisting of: -1 x Single-phase plug 230V 1P+N+E -1 x Three-phase plug 400V 3P+N+E | piece | 1 | 0 | 0
13,14 | SAPA metal flexible conduit Ø32 mm | piece | 3 | 0 | 0
13,15 | FeZn strip 30x4 mm for equipotential bonding, installed on the wall, paid per linear meter: | m | 20 | 0 | 0
13,16 | Equipotential bonding bar | piece | 1 | 0 | 0
13,17 | Tape-to-tape bonding clamp | piece | 10 | 0 | 0
13,18 | Bonding clamp tape-to-metal structure | piece | 10 | 0 | 0
13,19 | Testing of the installation, commissioning, and issuance of attestations and certificates from reputable manufacturers. Paid as a lump sum | lump sum | 1 | 0 | 0
| Total: |  |  |  | 0
RECAPITULATION
I | ELECTRICAL INSTALLATIONS
1 | POWER CABLES AND DISTRIBUTION BOARDS |  |  |  | 0
2 | ELECTRICAL INSTALLATIONS FOR LIGHTING |  |  |  | 0
3 | ELECTRICAL INSTALLATIONS FOR SOCKETS AND TECHNOLOGICAL CONNECTIONS |  |  |  | 0
4 | EMERGENCY LIGHTING INSTALLATIONS |  |  |  | 0
5 | CABLE TRAYS |  |  |  | 0
6 | Automatic Fire Alarm System |  |  |  | 0
7 | VIDEO SURVEILLANCE INSTALLATIONS |  |  |  | 0
8 | INSTALLATION FOR STRUCTURED CABLING (Internet and Telephone Installation) |  |  |  | 0
9 | INSTALLATION FOR ACCESS CONTROL |  |  |  | 0
10 | EQUALIZATION POTENTIAL INSTALLATIONS |  |  |  | 0
11 | PUBLIC ADDRESS AND VOICE ALARM SYSTEM |  |  |  | 0
12 | LIGHTNING PROTECTION AND PROTECTIVE GROUNDING |  |  |  | 0
13 | SPRINKLER STATION INSTALLATIONS |  |  |  | 0
TOTAL – ELECTRICAL INSTALLATIONS |  |  |  |  | 0
VAT 18% |  |  |  |  | 0
TOTAL INCLUDING VAT |  |  |  |  | 0

## 03. HVAC
ADMINISTRATIVE BUILDING - AGRI FOOD PLATFORM
Item No. | Pos. | Description | Unit | Quantity | Unit price (MKD) | TOTAL PRICE (MKD)
1 | 2 | 3 | 4 | 5 | 6 | 7
The basic unit prices, in addition to the basic purchase prices, also take into account the costs of transportation, loading, unloading, installation, manufacturing, etc.
1 |  | Main mechanical substation, common installation for fan coil heating and cooling and DHW preparation for the facility
| 1 | High temperature air to water heat pump, modular Scroll tehnology, with following specifications: • Nominal heat capacity mode A7/W45: min 143 kW (acc. EN14511) COP mode A7/W45: min 3,45 (acc. EN14511) • Heat capacity for the most unfavorable operating mode A-7/W55: min 115 kW ; • Nominal cooling capacity mode A35/W7: min 118 kW (acc. EN14511) EER mode A35/W7: min 2,87 (acc. EN14511) • 2 compressor circuits, R-410A refrigerant • Heating mode operation range: -15°C or lower • Maximum supply water temperature at Tsp= -15°C or lower: min 55°C • Heating mode operation range for outdoor temperatures of: -15°C do 40°C • Cooling mode operation for outdoor temperatures of: -10°C do 45°C • Sound power: max 88 dB, (acc. EN ISO9614-2) • Fan protection IP54 or better Electrical data for the worst operating conditions: Max. absorbed power: 63.7 kW; Full load Amps (F.L.A.) 111А. Max.starting current: 225 А. Set with capacitor for correction of cosf > 0.9 • With integrated hydro set module and 2 parallel frequency regulated circulation pumps with variable flow (4.3-13 l/s), which allows circulation to the heat exchanger • Dimensions: ~4400x1900x1800mm, Weight approx.: 1735 kg * BacNet, ModBus comunication protocols • The heat pump automation should enable simultaneous (i.e. parallel) heating of the boiler and cooling (or heating) in the buffer, starting and stopping of an external circulation pump (per exchanger) and control of a three-way valve (user side), according to temperature sensors in the tanks. • Operation fluid water-etylene glycol (70-30%) • Water filter • Rubber antivibration washers | piece | 1 | 0 | 0
| 2 | Buffer - storage tank for hot/cold water for fan coil heating and cooling - verticalско греење и ладење-вертикален Steel enamelled accumulator for hot and cold water storage, suitable for installation in closed circuit heating systems. 4 connections 4" R/G on 2 levels of flow direction, reducing inlet velocity and maintaining the layers of temperature, welded sleeves for probes on 2 levels. . Volume: 1000 l Allow.operating pressure: 6 bar Allow. operating temperature: 110 °C Manufactured in accordance with EU Directive 97/23/EG (Art.3,Abs.3) Dimensions: H= 2381mm, d=1160mm weight emty: 238 kg Completed with legs and thermal insulation min 100mm thickness, for heating/cooling storage tanks. Manufactured in accordance with the standard EN 60379 | piece | 1 | 0 | 0
| 3 | DHW storage tank for the kitchen and toilet for the kitchen employees - vertical Steel enamelled accumulator for hot water storage, suitable for installation in closed circuit heating systems. 8 connections 2" R/G on 4 levels of flow direction, reducing inlet velocity and maintaining the layers of temperature, welded sleeves for probes on 2 levels. Volume: 750 l Allow.operating pressure: 6 bar Allow.operating temperature: max.95 °C Manufactured in accordance with EU Directive 97/23/EG (Art.3,Abs.3) Dimensions: H= 1895mm, d=1004mm weight empty: 147 kg Completed with legs and thermal insulation min 100mm thickness, for heating storage tanks. Manufactured in accordance with the standard EN 60379 | piece | 1 | 0 | 0
| 4 | Manometer 0-16 bar, with accuracy class 1.6, diameter ф100, connection 1/2" | piece | 7 | 0 | 0
| 5 | Thermometer in a sleeve, mercury or alcohol, with a measuring range of 0-130 °C ° | piece | 6 | 0 | 0
| 6 | Expansion vessel 150l - for installation on fan coil heating and cooling system, Factory pre-pressured with nitrogen set at 1.5 bar, DIN-tested and authorizations in accordance with the Pressure Equipment Directive 97/23/EG. • маx. operating pressure: 10 bar • Operating temperature: -10 ÷ 99 °C Volume: 150 l • Pre-pressure set: 1,5 bar • Connection: 3/4" | piece | 1 | 0 | 0
| 7 | Electronic circulation pump with frequency regulation, set of connecting elements, flanges, counter-flanges, bolts, nuts, seals, for heating and cooling fan coil pipeline on header in technical room, temperature range from -10оС - 110оС with the following characteristics: | piece | 1 | 0 | 0
DN40 PN6/10
Q =14,4 m3/h,
dP=67,61 kPa
P = 17-608 W ( 1 x 230V, 50Hz)
Маx.absorbed electrical energy 0.19 - 2.78 А
| 8 | Electronic circulation pump with frequency regulation, set of connecting elements, flanges, counter-flanges, bolts, nuts, seals, for heating and cooling fan coil pipeline in kitchen and restaurant on header in technical room, temperature range from -10оС - 110оС with the following characteristics: | piece | 1 | 0 | 0
DN40 PN6/10
Q =5,9 m3/h,
dP=61,61 kPa
P = 17-267 W ( 1 x 230V, 50Hz)
Маx.absorbed electrical energy 0.19 - 1.26 А
| 9 | Safety valve with a spring for the installation of vessels for the accumulation of DHW water for kitchen, with a setting pressure of 6 bar, with dimensions:
|  | NPS 1/2" | piece | 1 | 0 | 0
| 10 | Safety valve with a spring for the installation on storage vessel for the accumulation of hot and cold water, with a setting pressure of 6 bar, with dimensions:
|  | NPS 1" | piece | 1 | 0 | 0
| 11 | Safety valve with a spring for mounting a pipeline for connecting expansion vessels, with a setting pressure of 6 bar, with dimensions
|  | NPS 3/4" | piece | 1 | 0 | 0
| 12 | Overflow valve, for use in heating systems with a max. operating temperature up to 1200C, for medium water and a mixture of water and water-glycol up to 57%, made of bronze body material, and a spring made of stainless steel, in accordance with EN ISO 4126 -1, with NPT female threaded ends per ANSI/ASME B1.20.1-1983. Pset = 3.0 barg and return pressure Pback=1.5 bar
|  | DN 20 | piece | 1 | 0 | 0
|  | DN 15 | piece | 1 | 0 | 0
| 13 | Freshwater module for wall mounting. Complete and factory-prepared station for comfortable and hygienic heating of DHW opearting on the principle of a flow-type heater. Minimum technical characteristics of the DHW module • nominal DHW flow at storage tank temperature of 55°C and DHW temperature of 45°C; from 41 to 45 l/min • ultrasonic sensor for volume flow measurement: 1-125 l.min • maximum working pressure at primary/secondary side:: 10 bar • min 3 temperature sensors Pt1000 - 1 on primary and 2 on secondary side • max allowed hardness of drinking water: min 20°dH * with a circulation pump on the side of the heating water (primary pump) - consumed power 70 до 100 W, 1ph, 230V * competed with power and signal cabling | piece | 1 |  | 0
0
| 14 | V-Bus communication cable for connecting the Freshwater module for hygienic DHW heating in a cascade. | m' | 50 | 0 | 0
| 15 | Two-way motorized valve for installing the cold water line for each module separately in the cascade - nominal diameter: DN 32 PN 10 - connections (external thread): G1¼” - Kvs value: 60 - electric motor drive: 1x230V; 0,6 kN; 3 point | piece | 1 | 0 | 0
| 16 | Balance and control motor valve, with the ability to measure energy, flow and temperature, complete with counter flanges, seals, nuts and screws, for max. working temperature up to 120 0C, for medium water and mixture of water and water-glycol up to 50 %, with body made of material GG25, spindle, ball and disc of stainless steel and sealing material PTFE and EPDM, with degree of protection IP54. Actuator is rated voltage AC/DC 24V, 50/60 Hz and power consumption during at work < 4.0 W. Communication control BACnet MS/TP Балансен и контролен моторен вентил, со можност за мерење на енергија, проток и температура на линија за греење/ладење кон кујна, комплет со контра прирабници, заптивки, навртки и завртки, за макс.работна температура до 120 0С, за медиум вода и мешавина на вода и вода-гликол до 50%, со тело изработено од материјал GG25, вретено, топка и диск од нерѓосувачки челик и заптивен материјал PTFE и EPDM, со степен на заштита IP54. Актуаторот е со номинален напон AC/DC 24V, 50/60 Hz и потрошувачка на енергија за време на работа 8.5 W. Комуникациска контрола BACnet MS/TP MP-Bus Modbus RTU, и димензии:
|  | DN40PN25 Kvs=12.3 | piece | 1 | 0 | 0
| 17 | Three-way motorized diverter valve with spring return actuator, for use in DHW heating and fancoils heating and cooling, for installation of a common supply and discharge line from heat pumps, in front of storage water heaters for DHW for a administrative building complete with connecting elements, flanges , counterflanges, screws, nuts, seals. The actuator is controlled by a 2-point signal with a spiral return function and is recommended for a diverting function, 230V AC, 50/60 Hz, connectors (flanged), electric motor drive: 1x230V; 0.6 kN; 3 points
|  | DN65PN16 Kvs=50 | piece | 1 | 0 | 0
| 18 | Flanged ball valve (for working medium water with tmax=110 °C, construction according to МКС EN 1983, made of carbon steel C25 or gray cast iron GS 240, installation lengths according to standard МКС EN 558-1 column 14, connecting dimensions of the flanges according to standard МКС EN 1092-1, test certificates according to МКС EN 12266-1,2 pressure testing P10, P11, P12 for material МКС EN10204 3.1, marks for CE marking according to PED91/23/EC) with set of counter flanges, seals, nuts and bolts.
|  | DN50PN10 | piece | 5 | 0 | 0
|  | DN65PN10 | piece | 3 | 0 | 0
|  | DN80PN10 | piece | 3 | 0 | 0
|  | DN100PN10 | piece | 10 | 0 | 0
| 19 | Threaded ball valve (operating temperature tmax=120 °C, operating pressure PN16, construction according to standard MKS EN 1983, tested according to standard MKS EN 12266, installation length according to EN558-1)
|  | NPT 1/2" | piece | 5 | 0 | 0
|  | NPT 3/4" | piece | 5 | 0 | 0
|  | NPT 1" | piece | 6 | 0 | 0
|  | NPT 1 1/4" | piece | 4 | 0 | 0
| 20 | Check (non-return) valve with set of flanges, counter flanges, seals, nuts and bolts (construction according to standard MKS EN 13709) for working medium water with Tmax = 120 0С
|  | DN25PN10 | piece | 1 | 0 | 0
|  | DN32PN10 | piece | 1 | 0 | 0
|  | DN65PN10 | piece | 1 | 0 | 0
|  | DN80PN10 | piece | 1 | 0 | 0
| 21 | Separator for ventilation and air separation, micro bubbles and oxygen in the heating and cooling system with a max. working temperature up to 120 0C, for medium water and a mixture of water and water-glycol up to 50%, made of steel, equipped with a bronze air separator and a drainage ball valve. Complete with flanges and counter-flanges according to MKS EN 1092-1, gaskets, nuts and bolts and insulation, with dimensions:
|  | DN50 PN10 | piece | 2 | 0 | 0
|  | DN65 PN10 | piece | 2 | 0 | 0
|  | DN80 PN10 | piece | 2 | 0 | 0
| 22 | Spirovent for dirt, sludge and metal particles, installed on the return line in the heating system with a max. working temperature up to 120 0C, for medium water and a mixture of water and water-glycol up to 50%, made of steel, equipped with two ball valves . The separator is with female threaded ends according to ASME B 1.20.1, with a steel handle, with PTFE seals and insulation, with dimensions:
|  | DN50 PN10 | piece | 2 | 0 | 0
|  | DN65 PN10 | piece | 2 | 0 | 0
|  | DN80 PN10 | piece | 2 | 0 | 0
| 23 | Automatic air venti with connection materials, R 1/2" | piece | 6 | 0 | 0
| 24 | Seamless steel tubes (seamless steel pipes),manufactured according to EN 10216-2, and fittings (elbows, reducers, couplings) ,with joining material included(electrodes, acetylene welding wire, oxygen, hinges) as well as material for fastening and hanging. The pipes shall be previously cleaned with a steel brush, coated twice with an anti-corrosion coating and insulated with layers of glass wool with a minimum density of 10 kg/m³ and a thickness of 80 mm for pipelines with dimensions DN50 and highere and 50 mm for pipelines with dimensions less then DN50, attached to the pipeline with a thin wire mesh, and on the outside wrapped and protected by an AI sheet metal with a thickness of δ=0.6 mm. Visible part to be painted with varnish paint. The visible part of the pipe network painted with varnish paint resistant to high temperature up to 110°C. The price includes joing material, material for fastening and hanging, cleaning, anti-corrosion caoating, insulation, visible pipes painting, everyting ready to work.
|  | DN 100 - Φ 114,3 x 3,6 - изолација 80 mm-надвор | m' | 8 | 0 | 0
|  | DN 25 - Φ 33,7 x 2,6 - изолација 50 mm-надвор | m' | 1 | 0 | 0
|  | DN 20 - Φ 26,9 x 2,3 - изолација 50 mm-надвор | m' | 1 | 0 | 0
| 25 | Seamless insulated black pipes and fittings (elbows, couplings , reducers), pipe network in the technical room and whole building (to the buffer and headers), manufactured according to DIN 2448 / EN 10220, with joint material (electrodes, acetylene welding wire), as well as fastening and hanging material (supports, brackets, holders, etc.). . The pipes must be previously cleaned with steel brushes, double-mined with an anti-corrosive coating. The pipes are insulated with insulation of the indicated thickness. The insulation must be self-extinguishing and prevent the spread of flame, according to EN13501-1 it must be at least class B(L)-s2, d0
|  | DN 200 - Φ 219,1 x 6,3 - insulation d = 32 mm | m' | 4 | 0 | 0
|  | DN 100 - Φ 114,3 x 3,6 - insulation d = 25 mm | m' | 52 | 0 | 0
|  | DN 50 - Φ 60,3 x 2,9 - insulation d = 19 mm | m' | 2 | 0 | 0
|  | DN 32 - Φ 42,4 x 2,6 - insulation d = 19 mm | m' | 12 | 0 | 0
|  | DN 25 - Φ 33,7 x 2,6 - insulation d = 13 mm | m' | 4 | 0 | 0
|  | DN 20 - Φ 26,9 x 2,3 - insulation d = 13 mm | m' | 2 | 0 | 0
* Note: Pipes with a dimensions range from DN40 to DN15 can also be seam with dimensions according to DIN 2440 / EN10255 and material S185.
| 26 | Concentric reducers for black pipes, from material P235GH, with dimensions acc. EN10253-1
|  | DN100/DN80 | piece | 6 | 0 | 0
|  | DN100/DN65 | piece | 3 | 0 | 0
|  | DN100/DN50 | piece | 2 | 0 | 0
|  | DN50/DN32 | piece | 2 | 0 | 0
|  | DN32/DN25 | piece | 2 | 0 | 0
|  | DN25/DN20 | piece | 4 | 0 | 0
| 27 | Antifreeze, propylene or ethylene glycol concentrate, long-lasting and biodegradable, with corrosion protection for the DHW preparation for students with heat pump HP3 • boiling point: above 150 ºC • freezing point: below -20 ºC • combustion point: > 100 ºC • pH- of a mixture with neutral water: 7,5 - 8,5 | L | 700 | 0 | 0
| 28 | Visual inspection and testing of the installation for strength and tightness (cold test) | lump sum | 1 | 0 | 0
| 29 | Balancing and commissioning (hot test) | lump sum | 1 | 0 | 0
| 30 | Manufacturing a protective cage for the heat pump (with dimensions 4000x3000x2100mm), made of profiled steel 60x60x5 mm and corrugated mesh with opening dimensions 30x30 and wire diameter 4.5mm | kg | 560 | 0 | 0
Total:
1. Main mechanical substation, common installation for fan coil heating and cooling and DHW preparation for the facility
|  |  | SUB TOTAL (MKD): |  |  | 0
|  |  | 18% VAT (MKD): |  |  | 0
|  |  | TOTAL 1 (MKD): |  |  | 0
NOTE: The remaining part for hot DHW water distribution and recirculation of hot DHW water from the boiler to the verticals, including valves and other additional material, is included in the plumbing bill of quantities.
2 |  | * Fan coil heating and cooling in Administrative building
Supply, transport, installation, calibration, testing and commissioning. The offered equipment should meet the minimum specified characteristics.
| 1 | Ceiling cassette fan coil unit with casing: made of galvanized steel and external anti-condensate coating, for two-pipe system, with high-efficiency exchanger made of copper pipes and aluminum fins, built-in fan with min. 3 speeds, side air intake, four-sided discharge, built-in air vent, condensate pump and Eurovent certified with the following characteristics or better:
| 1.1 | Dimensions: 575 x 575 x 275 Total cooling capacity: 1,60 kW (7/12°C), Heating capacity: 1,80 kW (45/40°C), Air flow: 420 m3/h, Water flow: 320 l/h (all parameters are at medium speed), Electrical data: Fan power 32 W ; IC 0.15A; 230V/1Ph/50Hz | piece | 5 | 0 | 0
| 1.2 | Dimensions: 575 x 575 x 275 Total cooling capacity: 3,30 kW (7/12°C), Heating capacity: 3,28 kW (45/40°C), Air flow: 500 m3/h, Water flow: 585 l/h (all parameters are at medium speed), Electrical data: Fan power 44 W ; IC 0.2A; 230V/1Ph/50Hz | piece | 7 | 0 | 0
| 1.3 | Dimensions: 575 x 575 x 275 Total cooling capacity 3,82 kW (7/12°C), Heating capacity: 3,85 kW (45/40°C), Air flow: 610 m3/h, Water flow: 682 l/h (all parameters are at medium speed), Electrical data: Fan power 57 W ; IC 0.27A ; 230V/1Ph/50Hz | piece | 5 | 0 | 0
| 1.4 | Dimensions: 820 x 820 x 303 Total cooling capacity 4,86 kW (7/12°C), Heating capacity: 5,03 kW (45/40°C), Air flow: 820 m3/h, Water flow: 891 l/h (all parameters are at medium speed),, Electrical data: Fan power 48 W ; IC 0.23A; 230V/1Ph/50Hz | piece | 7 | 0 | 0
| 2 | Digital thermostat with the ability to control actuators of fan coil units (3 fan speeds and valve actuator 230V ON/OFF), with so-called two-stage control, which allows setting the room temperature in heating mode, at which the floor heating starts, but also setting an interstage value, at which the second phase (fan coil and valve) are activated when the temperature difference is greater than the set interstage value (floor heating is not enough, turn on the fan coil). In cooling mode, the floor circuits are turned off, only the fan coil system functions. Programmable, with daily, weekly timer. | piece | 24 | 0 | 0
| 3 | Electric panel heater with thermostat Pel [nom]: 0.75/1,50 kW Protection: IP24 V/Ph+N/Hz: 220-240/1/50 | piece | 2 | 0 | 0
| 4 | Automatic air venti with connection materials, R 1/2" | piece | 12 | 0 | 0
| 5 | Combined balancing and control valve, with the possibility of differential pressure control, flow resetting, measurement, shut-off and draining. Intended for use in heating and cooling systems in small circuits, with a max. operating temperature of up to 1200C, for medium water and a mixture of water and water-glycol up to 57%, with body, cover and spindle made of AMETAL material, sealing material of EPDM O-ring seat, PTFE seals, stainless steel spring and polyamide handle, with NPT male threaded ends to ISO 228. The valve is completed with an actuator with voltage 24 VAC/VDC, input and output signal 0(2)-10 V, MODBUS communication and protection class IP54, valve connection M30x1.5, adjustment force of 125 N, protection class II , EN 60730, CE certified, EN 60730-2-14. Cold start time 4 min. Complete with connection cable 2x0.75 mm2 and length determined on site..
|  | DN15 PN16 | piece | 10 | 0 | 0
|  | DN20 PN16 | piece | 15 | 0 | 0
| 6 | Flanged ball valve (for working medium water with tmax=110 °C, construction according to МКС EN 1983, made of carbon steel C25 or gray cast iron GS 240, installation lengths according to standard МКС EN 558-1 column 14, connecting dimensions of the flanges according to standard МКС EN 1092-1, test certificates according to МКС EN 12266-1,2 pressure testing P10, P11, P12 for material МКС EN10204 3.1, marks for CE marking according to PED91/23/EC) with set of counter flanges, seals, nuts and bolts.
|  | DN50PN16 | piece | 2 | 0 | 0
|  | DN65PN16 | piece | 2 | 0 | 0
|  | DN80PN16 | piece | 3 | 0 | 0
| 7 | Threaded ball valve (operating temperature tmax=120 °C, operating pressure PN16, construction according to standard MKS EN 1983, tested according to standard MKS EN 12266, installation length according to EN558-1)
|  | DN15PN16 | piece | 10 | 0 | 0
|  | DN20PN16 | piece | 15 | 0 | 0
| 8 | Pipe reducing coupling, made of nickel/alloyed bronze material and manufactured according to EN 10242, for connection according to ISO 7-1, for use in heating systems with a maximum operating temperature of 0 to 1200C, with internally threaded ends according to ANSI/ASME B1.20.1-1983.
|  | 3/4" / 1/2“ | piece | 20 | 0 | 0
|  | 1" / 3/4“ | piece | 30 | 0 | 0
| 9 | Dilation compensators with welding, made of carbon steel S235JRH with compensating part of stainless steel material according to DIN EN 1.4541, for use in hot water heating systems with a max. operating temperature of up to 1200C, with an axial displacement of ± 20 mm
|  | DN80PN10 | piece | 2 | 0 | 0
|  | DN65PN10 | piece | 2 | 0 | 0
|  | DN50PN10 | piece | 4 | 0 | 0
|  | DN40PN10 | piece | 8 | 0 | 0
|  | DN32PN10 | piece | 6 | 0 | 0
|  | DN25PN10 | piece | 6 | 0 | 0
| 10 | Seamless steel tubes (saemless steel pipes) manufactured according to EN 10220 with fittings (elbows, reducers, couplings) , including joining material (electrodes, acetylene welding wire, oxygen, hinges), as well as material for fastening and hanging. The pipes shall be previously cleaned with a steel brush, coated twice with an anti-corrosion coating and insulatet with elastomeric insulation in tubes with thickness of d=19 mm(for pipe dimension up to DN80) and with thickness of d=13mm(for pipe dimension DN32 and less). Note: The insulation must be self-extinguishing and prevent the spread of flame according to BS476 Part 7/Class1, or according to EN13501-1 to be class B-s2,d0.
|  | DN 80 - Φ 88,9 x 3,2 | m' | 24 | 0 | 0
|  | DN 65 - Φ 76,1 x 2,9 | m' | 10 | 0 | 0
|  | DN 50 - Φ 60,3 x 2,9 | m' | 52 | 0 | 0
|  | DN 40 - Φ 48,3 x 2,6 | m' | 36 | 0 | 0
|  | DN 32 - Φ 42,4 x 2,6 | m' | 84 | 0 | 0
|  | DN 25 - Φ 33,7 x 2,6 | m' | 152 | 0 | 0
|  | DN 20 - Φ 26,9 x 2,3 | m' | 38 | 0 | 0
* Note: Pipes with a dimensions range from DN40 to DN15 can also be seam with dimensions according to DIN 2440 / EN10255 and material S185.
| 11 | Concentric reducers for black pipes, from material P235GH, with dimensions acc. EN10253-1
|  | DN80/DN65 | piece | 6 | 0 | 0
|  | DN80/DN40 | piece | 4 | 0 | 0
|  | DN65/DN50 | piece | 4 | 0 | 0
|  | DN50/DN40 | piece | 6 | 0 | 0
|  | DN50/DN32 | piece | 6 | 0 | 0
|  | DN40/DN32 | piece | 8 | 0 | 0
|  | DN32/DN25 | piece | 12 | 0 | 0
|  | DN32/DN20 | piece | 4 | 0 | 0
|  | DN25/DN20 | piece | 8 | 0 | 0
| 12 | Plastic PVC pipe for draining condensate, complete with joint, bearing and sealing material
|  | Ø25.4 | m' | 174 | 0 | 0
| 13 | Condensate drain trap DN20 for fan coil units to prevent the return of unpleasant odors, made of high-quality glass with self-cleaning properties, which prevents the formation of legionella, transparent with the possibility of easy detection of possible impurities and easy cleaning | piece | 24 | 0 | 0
| 14 | Testing, balancing and commissioning of the installation | lump sum | 1 | 0 | 0
2.Fan coil heating and cooling in Administrative building
|  |  | SUB TOTAL (MKD): |  |  | 0
|  |  | 18% VAT (MKD): |  |  | 0
|  |  | TOTAL 2 (MKD): |  |  | 0
3 |  | Ventilation of meeting room with HRU
Supply, transport, installation, calibration, testing and commissioning. The offered equipment should meet the minimum specified characteristics.
| 1 | Heat recovery unit (1100m3/hr), for indoor horizontal installation with the following elements and features or better: | set | 1 | 0 | 0
* Dimensions: (LхWхH) 1750x1150x385mm, weight 154kg
* EPS type thermal and acoustic panels with thermal bridge break. (min 25mm thickness of panels)
* Counter-flow plate heat exchanger, min80% thermal efficiency, in accordance with EU regulation 1253.
* External duct air water heater/cooler with heating capacity Qg=2,7 kW at 11oC (45/40oC) and cooling capacity Ql=5,3 kW at 32oC (7/12o/C), connected with the fan coil pipeline of the building and installed in the supply air duct
* With built-in electric duct heater with capacity Pel=3.0 kW; IC 13A;,which protects the exchanger from freezing at low temperatures Voltage 1/220/5
*The HR unit is with built-in control box, built-in temperature and humidity sensors, control for free cooling through motorized BY-PASS.
* Integrated filters: M5-exhaust air, F8-inlet air, according to EN779
*Exhaust single-speed fan built into the recuperator block, with air flow Q=1100 m3/h; and external pressure drop dPext=150 Pa; (the external pressure drop shown does not take into account the internal drops of the recuperator itself which should be calculated in the total pressure drop when selecting the fan)
*Supply single-speed fan built into the recuperator block, with air flow Q=1100 m3/h; and external pressure drop dPext=150 Pa; (the external pressure drop shown does not take into account the internal drops of the recuperator itself which should be calculated in the total pressure drop when selecting the fan)
*Pel[nom.] heat exchange and by-pass mode= 0,77 kW Electrical power during heat exchange and by-pass mode: 3.6A Voltage 1/220-240/50
*The filter and fan units have easy and simple access. The entire unit should be brought into the room before it is closed off with the reconstruction.
*CO2 and pressure sensor
*Room controller for managing the operation of the recuperator, with cabling
*Condesate pump
*Maximum sound power of the entire unit 45 dB(A). The unit is built into a suspended ceiling made of acoustic panels (covered in the architectural phase).
| 2 | Swirl square diffusers, complete with plenum box and flow regulator
|  | 600x600/24 (550m3/h) | piece | 2 | 0 | 0
| 3 | Square exhaust diffuser, complete with plenum box and flow regulator
|  | 600x600/24 (550m3/h) | piece | 2 | 0 | 0
| 4 | Flexible hose made of multiple laminated layers of aluminum and polyester with a steel spiral tape between them and with high tensile strength, complete with joint material
|  | Φ 250 | m' | 4 | 0 | 0
| 5 | Spiro pipes for connecting the vortex square diffusers to the plenum box, made of galvanized sheet with a Zn content of 140 g/m2, with insulation with dimensions:
|  | - Φ250 | m' | 4 | 0 | 0
| 6 | External aluminium protection louver, protection against atmospheric influences and insects
|  | 500x300 ; Aef=0.0975 m2 for (1100m3/h) | piece | 2 | 0 | 0
| 7 | Air distribution ducts made of galvanized steel sheet with thickness according to the duct cross-section complete with galvanized flanges,and included joining and sealing materijal,duct hangers and verical stiffening and shafts. In the specified "kg" the weight of the hanging and connection material is not calculated, but the unit price should include JOINING AND SEALING MATERIAL AND MATERIJAL FOR FASTENING AND HANGING. | kg | 390 | 0 | 0
| 8 | Elastomeric insulation in a roll for insulating air ducts with a thickness of d=19mm, complete with tape for insulating joints and adhesive. Note: The insulation must be self-extinguishing and prevent the spread of flame according to BS476 Part 7/Class1, or according to EN13501-1 it must be class B-s1,d1. Made of environmentally friendly material, free from materials harmful to human health such as: HCFC, formaldehydes | m2 | 56 | 0 | 0
| 9 | Revision openings 600x600 | piece | 1 | 0 | 0
| 10 | Plastic PVC pipe for draining condensate, complete with joint, bearing and sealing material
|  | Ø25.4 | m' | 10 | 0 | 0
| 11 | Setting the parameters, balancing, testing and putting the systems into trial operation with a report and finding that the set parameters have been achieved with the project, training of personnel for use and giving written instructions for the maintenance of the equipment | lump sum | 1 | 0 | 0
3.Ventilation of meeting room with HRU
|  |  | SUB TOTAL (MKD): |  |  | 0
|  |  | 18% VAT (MKD): |  |  | 0
|  |  | TOTAL 3 (MKD): |  |  | 0
4 |  | Ventilation of baths, toilets and wardrobes
Supply, transport, installation, calibration, testing and commissioning. The offered equipment should meet the minimum specified characteristics.
| 1 | Exhaust single-speed axial in-line fan, for bathrooms, complete with bearing elements and joint material, from a reputable manufacturer with the following characteristics: IPx4 protecion, Q= 295 m3/hr ; Pext=30Pa Pel= 24W / 1Ph/50Hz connection for PVC pipe Ø150, completed with aluminium external louver for weather and insect protection complete with 24 hour timer | piece | 1 | 0 | 0
| 2 | PVC pipe Ø150, complete with joint and supporting material | m' | 0.5 | 0 | 0
| 3 | Exhaust single-speed axial in-line fan complete with bearing elements and joint material, from a reputable manufacturer with the following characteristics:
* operating parameters: Vmin =300 m3/h dPext= 115 Pа
* weight: 6.2 kg
* rectangular connections inlet/outlet 150х300 mm
* thermal safety switch
* IP54
* Еlectrical data: Pel= 89 W ; IC 0.733A; 230V/50Hz/1Ph
|  | * complete with 24 hour timer | piece | 1 | 0 | 0
| 4 | Exhaust single-speed axial in-line fan complete with bearing elements and joint material, from a reputable manufacturer with the following characteristics:
* operating parameters: Vmin =375 m3/h dPext= 101 Pa
* weight: 6.2 kg
* rectangular connections inlet/outlet 150х300 mm
* thermal safety switch
* IP54
* Electrical data: Pel= 89 W ; IC 0.733A; 230V/50Hz/1Ph
|  | * complete with 24 hour timer | piece | 1 | 0 | 0
| 5 | Exhaust single-speed axial in-line fan complete with bearing elements and joint material, from a reputable manufacturer with the following characteristics:
* operating parameters: Vmin =600 m3/h dPext= 195 Pa
* weight: 10.7 kg
* rectangular connections inlet/outlet 200х400 mm
* thermal safety switch
* IP54
* Electrical data: Pel= 166 W ; IC 1.18A; 230V/50Hz/1Ph
|  | * complete with 24 hour timer | piece | 2 | 0 | 0
| 6 | External aluminium protection louver, protection against atmospheric influences and insects
|  | 400x150 ; Aef= 0.0348 m2 | piece | 1 | 0 | 0
|  | 400x200 ; Aef= 0.0492 m2 | piece | 1 | 0 | 0
|  | 500x200 ; Aef= 0.0615 m2 | piece | 2 | 0 | 0
| 7 | Aluminium ventilation grill for installation in the lower zone of the door, for pressure equalization, with dimensions and effective flow area:
|  | 325x125 ; Aef= 0.012 m2 | piece | 7 | 0 | 0
|  | 325x225 ; Aef= 0.024 m2 | piece | 2 | 0 | 0
|  | 425x325 ; Aef=0.048 m2 | piece | 1 | 0 | 0
| 8 | Ventilation disc air valves for toilet exhaust made of galvanized steel for installation in suspended ceilings RAL 9010/9016, complete with mounting frame
|  | Φ 100 | piece | 9 | 0 | 0
|  | Φ 125 | piece | 12 | 0 | 0
| 9 | PVC pipe ,complete with joint and supporting material
|  | Ø100 | m' | 2 | 0 | 0
|  | Ø125 | m' | 3 | 0 | 0
| 10 | Swivel clamps
|  | Φ 100 | piece | 9 | 0 | 0
|  | Φ 125 | piece | 12 | 0 | 0
| 11 | Flexible hose with joint material
|  | Φ 100 | m' | 18 | 0 | 0
|  | Φ 125 | m' | 20 | 0 | 0
| 12 | Air distribution ducts made of galvanized steel sheet with thickness according to the duct cross-section complete with galvanized flanges,and included joining and sealing materijal,duct hangers and verical stiffening ind shafts" THE PRICE INCLUDES JOINING AND SEALING MATERIAL AND MATERIAL FOR FASTENING AND HANGING | kg | 350 | 0 | 0
| 13 | Setting the parameters, balancing, testing and putting the systems into trial operation with a report and finding that the set parameters have been achieved with the project, training of personnel for use and giving written instructions for the maintenance of the equipment | lump sum | 1 | 0 | 0
4.Ventilation of baths, toilets and wardrobes
|  |  | SUB TOTAL (MKD): |  |  | 0
|  |  | 18% VAT (MKD): |  |  | 0
|  |  | TOTAL 4 (MKD): |  |  | 0
5 |  | HVAC installations in the kitchen and restaurant
5.1 |  | Ventilation with kitchen hoods and fresh air supply and treatment equipment
Supply, transport, installation, calibration, testing and commissioning. The offered equipment should meet the minimum specified characteristics.
| 1 | Central three-piece induction kitchen hood (hood) for ventilation of a hot block, without fresh air supply to it (it takes it from the space), made of stainless steel AISI 304, amount of air extracted from the hood 6200m3/h. The hood is manufactured according to the EN16282-62020 standard. | set | 1 | 0 | 0
* Hood dimensions: 3700x2800x500mm
* 3 rectangular exctract air connections 400x300mm with flow ragulation dampers
* Complete with 7 cyclone grease filter units to cover the entire suction surface of the hood, with 5 blind spots. The filters are cyclone, with high efficiency for removing particles, and are made of al. sheet and are easy to dismantle for cleaning and replacement. Typical filter surface treatment: anodic oxidation in natural aluminum color.
* The hood must be equipped with an UV Ozone System, a system for maintaining hygienic conditions inside the hood and kitchen exhaust ducts, reduction of unpleasant odors and elimination of fat deposits, for the amount of extracted air 6200m3/hr. The system consists of adequate number of lamps for the extracted air, control cabinet (600x400x210mm) with HMI interface and stainless steel hangers, air flow sensor and magnetic switches. Power and signal cabeling of the system between the cabinet and the lamp included. IP54 protection. Nominal power <1150 W. Minimum 10000 operation hours before the needed replacement of the lamps.
* 6 lamps x 10 W with lamp length min 720mm
*The fire suppresion system for hood#1. The basic system consists of a regulated liquid agent release assembly, electric or manual, which includes a regulated release mechanism and a liquid agent storage tank located in an enclosure. Nozzles, detectors, cartridges, fluid, fusible links, pulley t-pieces and pulley elbows, pipe network, sensors, are delivered in separate packages in quantities required for each separate arrangement of the fire extinguishing system. (The system can be one, two, three or more tanks. Which type of system will be applied, including pipe dimensions, number and type of sprinklers, total capacity of the restaurant fire extinguishing system is determined based on performed / built-in kitchen appliances in the hot block in the kitchen, because of which the final appearance and capacity of the system will be determined after the installation of the kitchen appliances).
* The hood should be multi-part due to the limited possibility of bringing it into the room. . Maximum openings in the room 1.0 x 2.2m (door).
| 2 | Wall single-sided induction kitchen hood for ventilation of a hot block, without fresh air supply (it takes it from the space), made of stainless steel AISI 304, amount of exhaust air from the hood 800 m3/h. The hood is manufactured according to the EN16282-62020 standard. | set | 1 | 0 | 0
* Hood dimensions: 1300x1500x500mm
* 1 rectangular exctract air connection 300x200mm
* Complete with 1 cyclone grease filter unit to cover the entire suction surface of the hood, with 1 blind spot. The filters are cyclone, with high efficiency for removing particles, are made of al. sheet and are easy to dismantle for cleaning and replacement.. Typical surface treatment of the filter: anodic oxidation in natural aluminum color.
*The hood must be equipped with an UV Ozone System, a system for maintaining hygienic conditions inside the hood and kitchen exhaust ducts, reduction of unpleasant odors and elimination of fat deposits, for the amount of extracted air 800m3/hr. The system consists of adequate number of lamps for the extracted air, control cabinet (600x400x210mm) with HMI interface and stainless steel hangers, air flow sensor and magnetic switches. Power and signal cabeling of the system between the cabinet and the lamp included. IP54 protection. Nominal power <500 W. Minimum 10000 operation hours before the needed replacement of the lamps.
* 2 lamps x 10 W with lamp lenght min 720mm
* The hood should be multi-part due to the limited possibility of bringing it into the room. . Maximum openings in the room 1.0 x 2.2m (door).
| 3 | Wall single-sided kitchen hood (hood made of AISI 304/EN 1.4301, according to standard EN 16282-2_2016, amount of exhaust air from the hood 590 m3/h | set | 1 | 0 | 0
* Hood dimensions:: 600x450x750mm
* 1 circular exctract air connection Ø150mm
* 2 LED lamps 60lux x 1 W
* dPext= 220 Pa
- Pel [max]= 212 W
- V; Hz; Ph: 220-240V;50; ~1
* The hood should be able to be brought into the room. Maximum openings in the room 1.0 x 2.2m (door).
| 4 | Single-speed extract roof fan for kitchen hood, with base and flexible fire-resistant connection included, continuous operation at exhaust air temperature of 120°C, motor outside the air stream in accordance with VDI 2053 guidelines, vertical exhaust, integrated service assembly and condensate and grease collector, complete with automatic closure, safety thermo-switch: | piece | 1 | 0 | 0
- Q= 6200 m3/h
- dPext= 255 Pa
W=113 kg
IP=55
- Pel [max]= 2467 W
- V; Hz; Ph: 400V;50; ~3; IC 4.28 A; SC 37 A
| 5 | Single-speed extract roof fan for kitchen hood #3, with base and flexible fire-resistant connection included, continuous operation at exhaust air temperature of 120°C, motor outside the air stream in accordance with VDI 2053 guidelines, vertical exhaust, integrated service assembly and condensate and grease collector, complete with automatic closure, safety thermo-switch: | piece | 1 | 0 | 0
- Q= 800 m3/h
- dPext= 179 Pa
W=31.5 kg
IP=55
- Pel [max]= 345 W
- V; Hz; Ph: 400V;50; ~3; IC 0.86 A; SC 14.1 A
| 6 | VRF outdoor unit with the following technical characteristics: ••• Heat capacity for heating mode: nom. 56.0 kW (according to EN14511) • COP for heating mode: 4.43 (according to EN14511) • Cooling capacity: 56.0 kW (according to EN14511) • EER for cooling mode: 3.19 (according to EN14511) • SCOP for heating mode: 5.13 (according to EN14511) • SEER for cooling mode: 8.42 (according to EN14511) • Number of compressors: 2 with soft starter • Number of fans and power: 2 (0.9+0.9 kW) • Fans in protection IP54 or higher • Operation in heating mode at outdoor conditions: -30°C to 18°C • Operation in cooling mode at outdoor conditions: -15°C to 52°C • Sound power: max 64 dB (according to ISO3744) • Refrigerant R410A • Possibility of operating min. 3 indoor fresh air units with a total capacity of 50-100% of that of the outdoor unit | set | 1 | 0 | 0
Electrical data of the VRF outdoor unit: • Pel heating (nom.) = 12.64 kW • Pel cooling (nom.) = 17.54 kW • Min. current rating = 45.5 A • Total current rating = 50 A • Max. fuse rating = 50 A • Soft starter - built-in • Compressor-heating rated current = 18.2 A • Compressor-cooling rated current = 26.2 A • Fans rated current = 2.5x2 A
Control and management: * Control and management of the external VRF unit with the internal units, communication protocols * Sensors distributed throughout the freon lines that ensure stable operation and reliability of the system * Possibility for external units to distribute addresses to internal units * Possibility for independent control and power supply of each internal unit, etc.
| 7 | VRF outdoor unit with the following technical characteristics: ••• Heat capacity for heating mode: nom. 44.0 kW (according to EN14511) • COP for heating mode: 4.44 (according to EN14511) • Cooling capacity: 44.80 kW (according to EN14511) • EER for cooling mode: 2.90 (according to EN14511) • SCOP for heating mode: 5.46 (according to EN14511) • SEER for cooling mode: 7.97 (according to EN14511) • Number of compressors: 2 with soft starter • Number of fans and power: 2 (0.9+0.9 kW) • Fans with protection IP54 or higher • Operation in heating mode at outdoor conditions: -30°C to 18°C • Operation in cooling mode at outdoor conditions: -15°C to 52°C • Sound power: max 62 dB (according to ISO3744) • Refrigerant R410A • Possibility of operating min. 3 indoor fresh air units with a total capacity of 50-100% of that of the outdoor unit | set | 1 | 0 | 0
Electrical characteristics of the VRF outdoor unit: • Pel heating (nom.) = 10.09 kW • Pel cooling (nom.) = 15.45 kW • Min. current rating = 27.3 A • Total current rating = 30 A • Max. fuse rating = 32 A • Soft starter - built-in • Compressor-heating rated current = 14.0 A • Compressor-cooling rated current = 22.7 A • Fans rated current = 2.5x2 A
Control and management: * Control and management of the external VRF unit with the internal units, communication protocols * Sensors distributed throughout the freon lines that ensure stable operation and reliability of the system * Possibility for external units to distribute addresses to internal units * Possibility for independent control and power supply of each internal unit, etc.
| 8 | Indoor fresh air unit, with built-in freon heat exchanger for heating/cooling, with the following features | piece | 3 | 0 | 0
- Cooling capacity: 28 kW
- Heating capacity: 26.7 kW
- Q=2142 m3/h
- dPext= 216 Pa
- W=73 kg
- Pel cooling/heating [max]=360 W
- V; Hz; Ph: 220-240V;50;~1;
| 9 | Material for connecting the outdoor units to the indoor units. It is noted that the selection of the equipment - outdoor and indoor fresh air units - is made software-based, so the material for connecting the outdoor and indoor units is selected accordingly. NOTE: THE SUPPLIER OF OTHER EQUIPMENT SHALL PROVIDE A SOFTWARE SELECTION FOR THE EQUIPMENT - OUTDOOR AND INDOOR FRESH AIR UNITS AND COMPLETE CONNECTION MATERIAL. THE MATERIAL SUPPLIED IN THE BILL IS A SOFTWARE SELECTION FROM A SPECIFIC MANUFACTURER
| 9.1 | Copper insulated pipes - copper alloy Cu DHP 99.90 min., with dimensions and tolerances according to EN 12735-1, corrosion resistant, with insulation from expanded polyethylene PE with thickness: for pipes from Φ6.35~Φ38.1 ≥15, Φ41.3~Φ38.1 ≥20, fire resistance - self-extinguishing according to M1 certification, thermal conductivity at 40°C =<0.040 W/m K, density approx. 30 kg/m³, for operating temperature from -70° + 120°C, suitable for freon R410A
| 9.1.1 | Φ 9,52 x 0,81 / ellbows 7 - liquid | m' | 20 | 0 | 0
| 9.1.2 | Φ 12,7 x 0,81 / ellbow 1 - liquid | m' | 1 | 0 | 0
| 9.1.3 | Φ 15,9 x 0,81 / ellbows 4 - liquid | m' | 5.5 | 0 | 0
| 9.1.4 | Φ 19,1 x 0.89 / ellbows 2 - liquid | m' | 8 | 0 | 0
| 9.1.5 | Φ 22,2 x 0,89 / ellbows 7 - gas | m' | 20 | 0 | 0
| 9.1.6 | Φ 28,6 x 0,89 / ellbows 4 - gas | m' | 6.5 | 0 | 0
| 9.1.7 | Φ 41,3 x 1,1 / ellbows 2 - gas | m' | 8 | 0 | 0
| 9.2 | Copper insulated Y branch - made of copper alloy Cu DHP 99.90 min., with dimensions and tolerances according to EN 12735-1, corrosion resistant, with insulation of expanded polyethylene PE with thickness: for pipes from Φ6.35~Φ38.1 ≥15, Φ41.3~Φ38.1 ≥20, fire resistance - self-extinguishing according to M1 certification, thermal conductivity at 40°C =<0.040 W/m K, density approx. 30 kg/m³, for operating temperature from -70° + 120°C, suitable for freon R410A
| 9.2.1 | Φ 9,52 - Φ 9,52 / Φ 15,9 - liquid | piece | 1 | 0 | 0
| 9.2.2 | Φ 9,52 - Φ 15,9 / Φ 19,1 - liquid | piece | 1 | 0 | 0
| 9.2.3 | Φ 12,7 - Φ 15,9 / Φ 19,1 - liquid | piece | 1 | 0 | 0
| 9.2.4 | Φ 22,2 - Φ 22,2 / Φ 28,6 - gas | piece | 1 | 0 | 0
| 9.2.5 | Φ 22,2 - Φ 28,6 / Φ 41,3 - gas | piece | 1 | 0 | 0
| 9.2.6 | Φ 28,3 - Φ 28,6 / Φ 41,3 - gas | piece | 1 | 0 | 0
| 10 | Duct cassette filter class F8 according to EN 779: 2012 standard, with maximum dimensions:
|  | - 500x300x390 mm for 2142 m3/h , initial pressure drop <80 Pa | piece | 3 | 0 | 0
| 11 | Perforated aluminum diffuser for wall and ceiling installation with flow regulator, suitable for kitchens, laboratories, etc. with minimal effective flow area
|  | l=1200 mm ; Aef=0.39 m2 for (2142m3/h) - wall | piece | 2 | 0 | 0
|  | l=1200 mm ; Aef=0.39 m2 for (2142m3/h) - central | piece | 1 | 0 | 0
| 12 | External aluminium protection louver, protection against atmospheric influences and insects
|  | 500x200 ; Aef=0.615 m2 for (590m3/h) | piece | 1 | 0 | 0
|  | 1000x300 ; Aef=0.195 m2 for (2142m3/h) | piece | 1 | 0 | 0
|  | 800x400 ; Aef=0.2136 m2 for (2142m3/h) | piece | 2 | 0 | 0
| 13 | Air distribution ducts made of galvanized steel sheet with thickness according to the duct cross-section complete with galvanized flanges,and included joining and sealing materijal,duct hangers and verical stiffening ind shafts" THE PRICE INCLUDES JOINING AND SEALING MATERIAL AND MATERIAL FOR FASTENING AND HANGING | kg | 273 | 0 | 0
| 14 | Exhaust air distribution ducts, exhaust from eco-type kitchen hoods, made of galvanized steel sheet with a minimum thickness of 1.15 mm complete with galvanized flanges of suitable thickness ,and included joining and sealing materijal,duct hangers and verical stiffening in shafts. In the specified "kg" the weight of the hanging and connection material is not calculated, but the unit price should include JOINING AND SEALING MATERIAL AND MATERIJAL FOR FASTENING AND HANGING. | kg | 375 | 0 | 0
| 15 | Flexible hoses for connecting the exhaust ducts with the exhaust roof fans made of Al+PEt, with 25mm insulation and temperature range: -30oC-140oC with dimensions:
|  | - Φ630 l=1000mm | piece | 1 | 0 | 0
|  | - Φ438 l=1000mm | piece | 1 | 0 | 0
|  | - Φ150 l=1700mm | piece | 1 | 0 | 0
| 16 | Plastic PVC pipe for draining condensate, complete with joint, bearing and sealing material
|  | Ø25 x 1,5 | m' | 7 | 0 | 0
|  | Ø32 x 1,8 | m' | 1 | 0 | 0
| 17 | Fireproof insulation according to standard EN1366-1, EN 13501-1, class A2-s1 d0, for fire resistance EI90, from mineral wool with a minimum thickness of 60mm with a melting point > 1000°C, density min 100 kg/m3 wrapped with aluminum foil and properly secured (for insulation of extract ducts of eco-type hoods) | m2 | 60 | 0 | 0
| 18 | Elastomeric insulation in a sheet for insulating air ducts with a thickness of d=19mm (fresh air ducts in the kitchen), complete with tape for insulating the joints and an adhesive.. Note: The insulation must be self-extinguishing and prevent the spread of flames according to BS476 Part 7/Class1, or according to EN13501- 1 to be class B-s3, d0. Made of environmentally friendly material, free from materials harmful to human health such as: HCFC, formaldehydes | m2 | 40 | 0 | 0
| 19 | Passive fire protection of penetrations through fire walls, with fireproof coating or fireproof plaster, according to standard EN 1366-3) | m3 | 10 | 0 | 0
| 20 | Material for installing of exhaust roof fans from hoods 1 and 2 made of hot-rolled steel UPN-65 from carbon steel material S235RJ, with dimensions according to EN 10365, with complete anti-corrosion protection and painting with high temperature resistant paint | kg | 190 | 0 | 0
| 21 | Setting the parameters, balancing, testing and putting the systems into trial operation with a report and finding that the set parameters have been achieved with the project, training of personnel for use and giving written instructions for the maintenance of the equipment | lump sum | 1 | 0 | 0
|  | 5.1Ventilation with kitchen hoods and fresh air supply and treatment equipment |  |  |  | 0
5.2 |  | Automatic regulation for setting and maintaining the pressure air tempreture for a kitchen hood
| 1 | Duct/immersion temperature sensor with the following technical characteristics: NTC 10k, L=200 mm, d=6 mm | piece | 2 | 0 | 0
| 2 | Remote control controller with built-in display and the following technical features DI8, AI8, DO 8, AO 4, 24 V AC/DC, seven fan speed controls in the indoor fresh air units, with the possibility of expansion with input-output modules and with the possibility of further integration into the BMS via Modbus TCP and BACnet IP | piece | 1 | 0 | 0
| 3 | Control cabinet for automatic regulation intended for wall mounting, with necessary equipment for current and voltage protection, complete with: transformer, relays, switches, lamps, terminals and other installation material, completely wired and tested | piece | 1 | 0 | 0
| 4 | Power and signal cabling | lump sum | 1 | 0 | 0
| 5 | Testing, commissioning, parameter setting and adjustment | lump sum | 1 | 0 | 0
| 6 | Preparation of an as-built project | lump sum | 1 | 0 | 0
| 7 | Development of user manual and staff training | lump sum | 1 | 0 | 0
5.2Automatic regulation for setting and maintaining the pressure air tempreture for a kitchen hood
5.3 |  | Fan coil heating and cooling for kitchen and restaurant
Procurement, transport, installation:
| 1 | Floor-standing fan coilers with a cabinet, for a two-pipe system, with a high-efficiency heat exchanger made of copper pipes and aluminum lamellas, a built-in fan with min. 3 speeds, side air intake, vertical thrust, built-in bleed valve Eurovent certified with the following features or better:
| 1.1 | Dimensions: 1415 x 630 x 225 Total cooling capacity (7/12°C) 5,09 kW , Heating capacity (45/40°C) 5,75 kW, Air flow 815 m3/h, Water flow 955 l/h (all parameters are at medium speed), Electrical data: Fan power 105 W ; 230V/1Ph/50Hz | piece | 2 | 0 | 0
| 2 | Ceiling cassette fan coil unit with casing: made of galvanized steel and external anti-condensate coating, for two-pipe system, with high-efficiency exchanger made of copper pipes and aluminum fins, built-in fan with min. 3 speeds, side air intake, four-sided discharge, built-in air vent, condensate pump and Eurovent certified with the following characteristics or better:
| 2.1 | Dimensions: 575 x 575 x 275 Total cooling capacity: 1,60 kW (7/12°C), Heating capacity: 1,80 kW (45/40°C), Air flow: 420 m3/h, Water flow: 320 l/h (all parameters are at medium speed), Electrical data: Fan power 32 W ; IC 0.15A; 230V/1Ph/50Hz | piece | 1 | 0 | 0
| 2.2 | Dimensions: 575 x 575 x 275 Total cooling capacity 3,82 kW (7/12°C), Heating capacity: 3,85 kW (45/40°C), Air flow: 610 m3/h, Water flow: 682 l/h (all parameters are at medium speed), Electrical data: Fan power 57 W ; IC 0.27A ; 230V/1Ph/50Hz | piece | 4 | 0 | 0
| 3 | Digital thermostat with the ability to control actuators of fan coil units (3 fan speeds and valve actuator 230V ON/OFF), with so-called two-stage control, which allows setting the room temperature in heating mode, at which the floor heating starts, but also setting an interstage value, at which the second phase (fan coil and valve) are activated when the temperature difference is greater than the set interstage value (floor heating is not enough, turn on the fan coil). In cooling mode, the floor circuits are turned off, only the fan coil system functions. Programmable, with daily, weekly timer. | piece | 4 | 0 | 0
| 4 | Automatic air venti with connection materials, R 1/2" | piece | 6 | 0 | 0
| 5 | Combined balancing and control valve, with the possibility of differential pressure control, flow resetting, measurement, shut-off and draining. Intended for use in heating and cooling systems in small circuits, with a max. operating temperature of up to 1200C, for medium water and a mixture of water and water-glycol up to 57%, with body, cover and spindle made of AMETAL material, sealing material of EPDM O-ring seat, PTFE seals, stainless steel spring and polyamide handle, with NPT male threaded ends to ISO 228. The valve is completed with an actuator with voltage 24 VAC/VDC, input and output signal 0(2)-10 V, MODBUS communication and protection class IP54, valve connection M30x1.5, adjustment force of 125 N, protection class II , EN 60730, CE certified, EN 60730-2-14. Cold start time 4 min. Complete with connection cable 2x0.75 mm2 and length determined on site..
|  | DN15 PN16 | piece | 1 | 0 | 0
|  | DN20 PN16 | piece | 4 | 0 | 0
|  | DN25 PN16 | piece | 1 | 0 | 0
| 6 | Flanged ball valve (for working medium water with tmax=110 °C, construction according to МКС EN 1983, made of carbon steel C25 or gray cast iron GS 240, installation lengths according to standard МКС EN 558-1 column 14, connecting dimensions of the flanges according to standard МКС EN 1092-1, test certificates according to МКС EN 12266-1,2 pressure testing P10, P11, P12 for material МКС EN10204 3.1, marks for CE marking according to PED91/23/EC) with set of counter flanges, seals, nuts and bolts.
|  | DN50PN16 | piece | 2 | 0 | 0
| 7 | Threaded ball valve (operating temperature tmax=120 °C, operating pressure PN16, construction according to standard MKS EN 1983, tested according to standard MKS EN 12266, installation length according to EN558-1)
|  | DN15PN16 | piece | 1 | 0 | 0
|  | DN20PN16 | piece | 4 | 0 | 0
|  | DN25PN16 | piece | 1 | 0 | 0
| 8 | Pipe reducing coupling, made of nickel/alloyed bronze material and manufactured according to EN 10242, for connection according to ISO 7-1, for use in heating systems with a maximum operating temperature of 0 to 1200C, with internally threaded ends according to ANSI/ASME B1.20.1-1983.
|  | 3/4" / 1/2“ | piece | 2 | 0 | 0
|  | 1" / 3/4“ | piece | 8 | 0 | 0
|  | 1 1/4" / 1“ | piece | 2 | 0 | 0
| 9 | Overflow valve, for use in heating systems with a max. operating temperature up to 1200C, for medium water and a mixture of water and water-glycol up to 57%, made of bronze body material, and a spring made of stainless steel, in accordance with EN ISO 4126 -1, with NPT female threaded ends per ANSI/ASME B1.20.1-1983. Pset = 3.0 barg and return pressure Pback=1.5 bar
|  | DN15PN10 | piece | 1 | 0 | 0
| 10 | Dilation compensators with welding, made of carbon steel S235JRH with compensating part of stainless steel material according to DIN EN 1.4541, for use in hot water heating systems with a max. operating temperature of up to 1200C, with an axial displacement of ± 20 mm
|  | DN50PN10 | piece | 1 | 0 | 0
|  | DN40PN10 | piece | 1 | 0 | 0
|  | DN32PN10 | piece | 2 | 0 | 0
| 11 | Seamless steel tubes (saemless steel pipes) manufactured according to EN 10220 with fittings (elbows, reducers, couplings) , including joining material (electrodes, acetylene welding wire, oxygen, hinges), as well as material for fastening and hanging. The pipes shall be previously cleaned with a steel brush, coated twice with an anti-corrosion coating and insulatet with elastomeric insulation in tubes with thickness of d=19 mm(for pipe dimension up to DN80) and with thickness of d=13mm(for pipe dimension DN32 and less). Note: The insulation must be self-extinguishing and prevent the spread of flame according to BS476 Part 7/Class1, or according to EN13501-1 to be class B-s2,d0.
|  | DN 65 - Φ 76,1 x 2,9 | m' | 14 | 0 | 0
|  | DN 40 - Φ 48,3 x 2,6 | m' | 32 | 0 | 0
|  | DN 32 - Φ 42,4 x 2,6 | m' | 26 | 0 | 0
|  | DN 25 - Φ 33,7 x 2,6 | m' | 32 | 0 | 0
|  | DN 20 - Φ 26,9 x 2,3 | m' | 4 | 0 | 0
* Note: Pipes with a dimensions range from DN40 to DN15 can also be seam with dimensions according to DIN 2440 / EN10255 and material S185.
| 12 | Concentric reducers for black pipes, from material P235GH, with dimensions acc. EN10253-1
|  | DN65/DN40 | piece | 4 | 0 | 0
|  | DN40/DN32 | piece | 4 | 0 | 0
|  | DN40/DN25 | piece | 2 | 0 | 0
|  | DN40/DN20 | piece | 2 | 0 | 0
|  | DN32/DN25 | piece | 10 | 0 | 0
| 13 | Plastic PVC pipe for draining condensate, complete with joint, bearing and sealing material
|  | Ø25.4 | m' | 32 | 0 | 0
| 14 | Condensate drain trap DN20 for fan coil units to prevent the return of unpleasant odors, made of high-quality glass with self-cleaning properties, which prevents the formation of legionella, transparent with the possibility of easy detection of possible impurities and easy cleaning | piece | 5 | 0 | 0
| 15 | Testing, balancing and commissioning of the installation | lump sum | 1 | 0 | 0
|  | 5.3 Fan coil heating and cooling for kitchen and restaurant |  |  |  | 0
5.4 |  | Ventilation of restaurant with HRU
Procurement, transport, installation:
| 1 | Heat recovery unit (1700m3/hr), for indoor horizontal installation with the following elements and features or better: | set | 1 | 0 | 0
* Dimensions: (LхWхH) 2100x1250x470mm, weight 180kg
* EPS type thermal and acoustic panels with thermal bridge break. (min 25mm thickness of panels)
* Counter-flow plate heat exchanger, min80% thermal efficiency, in accordance with EU regulation 1253.
* External duct air water heater/cooler with heating capacity Qg=4,0 kW at 11oC (45/40oC) and cooling capacity Ql=8,4 kW at 32oC (7/12o/C), connected with the fan coil pipeline of the building and installed in the supply air duct
* With built-in electric duct heater with capacity Pel=6,0 kW; IC 8,7A, which protects the exchanger from freezing at low temperatures Voltage 3/400/50
*The HR unit is with built-in control box, built-in temperature and humidity sensors, control for free cooling through motorized BY-PASS.
* ntegrated filters: M5-exhaust air, F8-inlet air, according to EN779
*Exhaust single-speed fan built into the recuperator block, with air flow Q=1700 m3/h; and external pressure drop dPext=220 Pa; (the external pressure drop shown does not take into account the internal drops of the recuperator itself which should be calculated in the total pressure drop when selecting the fan)
*Supply single-speed fan built into the recuperator block, with air flow Q=1700 m3/h; and external pressure drop dPext=220 Pa; (the external pressure drop shown does not take into account the internal drops of the recuperator itself which should be calculated in the total pressure drop when selecting the fan)
*Pel[nom.] heat exchange and by-pass mode= 1,06 kW Electrical power during heat exchange and by-pass mode:4.7A Voltage 1/220-240/50
*The filter and fan units have easy and simple access. The entire unit should be brought into the room before it is closed off with the reconstruction.
* CO2 and pressure sensors
*Room controller for managing the operation of the recuperator, with cabling
*Condesate pump
*Maximum sound power of the entire unit 45 dB(A). The unit is built into a suspended ceiling made of acoustic panels (covered in the architectural phase)
| 2 | Swirl square diffusers, complete with plenum box and flow regulator
|  | 600x600/24 (560m3/h) | piece | 3 | 0 | 0
| 3 | Square exhaust diffuser, complete with plenum box and flow regulator
|  | 600x600/24 (560m3/h) | piece | 3 | 0 | 0
| 4 | Spiro pipes for connecting the vortex square diffusers to the plenum box, made of galvanized sheet with a Zn content of 140 g/m2, with insulation with dimensions:
|  | - Φ250 | m' | 6 | 0 | 0
| 5 | External aluminium protection louver, protection against atmospheric influences and insects
|  | 700x400 ; Aef=0.1869 m2 за (1700m3/h) | piece | 2 | 0 | 0
| 6 | Air distribution ducts made of galvanized steel sheet with thickness according to the duct cross-section complete with galvanized flanges,and included joining and sealing materijal,duct hangers and verical stiffening and shafts. In the specified "kg" the weight of the hanging and connection material is not calculated, but the unit price should include JOINING AND SEALING MATERIAL AND MATERIJAL FOR FASTENING AND HANGING. | kg | 580 | 0 | 0
| 7 | Elastomeric insulation in a roll for insulating air ducts with a thickness of d=19mm, complete with tape for insulating joints and adhesive. Note: The insulation must be self-extinguishing and prevent the spread of flame according to BS476 Part 7/Class1, or according to EN13501-1 it must be class B-s1,d1. Made of environmentally friendly material, free from materials harmful to human health such as: HCFC, formaldehydes | m2 | 90 | 0 | 0
| 8 | Revision openings 600x600 | piece | 1 | 0 | 0
| 9 | Plastic PVC pipe for draining condensate, complete with joint, bearing and sealing material
|  | Ø25.4 | m' | 3 | 0 | 0
| 10 | Setting the parameters, balancing, testing and putting the systems into trial operation with a report and finding that the set parameters have been achieved with the project, training of personnel for use and giving written instructions for the maintenance of the equipment | lump sum | 1 | 0 | 0
|  | 5.4 Ventilation of restaurant with HRU: |  |  |  | 0
5. HVAC installations in the kitchen and restaurant:
|  |  | SUB TOTAL (MKD): |  |  | 0
|  |  | 18% VAT (MKD): |  |  | 0
|  |  | TOTAL 5 (MKD): |  |  | 0
|  | SUMMARY |  |  |  | MKD
1 |  | Main mechanical substation, common installation for fan coil heating and cooling and DHW preparation for the facility |  |  |  | 0
2 |  | Fan coil heating and cooling in Administrative building |  |  |  | 0
3 |  | Ventilation of meeting room with HRU |  |  |  | 0
4 |  | Ventilation of baths, toilets and wardrobes |  |  |  | 0
5 |  | HVAC installations in the kitchen and restaurant |  |  |  | 0
TOTAL (MKD): | [5 empty] | 0
18% VAT (MKD): | [5 empty] | 0
TOTAL 1-5 (MKD): | [5 empty] | 0

## 04. WSS
Bill of Quantities for the construnction of a complex facilities for the trade center - AGRI FOOD PLATFORM, for building purpose B2, at B.P. 12.1 (administrative building), MUNICIPALITY GAZI BABA, SKOPJE
Item No. | DESCRIPTION | Unit | Quantity | Unit price | Total Price
NOTE: For descriptions that refer to a manufacturer or standard, "equivalent" applies, but the product/material offered as a replacement should have the same or better characteristics than those listed in the description. It is valid for all positions of the bill of quantities.
WATER SUPPLY AND SEWAGE
1 | WATER SUPPLY INSTALLATION
1.1. | External water supply (from building to water meter shaft)
1 | Marking of route according to technical regulations for earthworks. | m' | 10.35 | 0 | 0
2 | Combined excavation, manual and machine, of earth material in III and IV category of earth according to GN200 categorization, for placing pipeline into trench with width up to 1.20m and depth 0-2.0m. Total V=7,45m3 from which:
| machine 80% | m3 | 5.9616 | 0 | 0
| manual 20% | m3 | 1.4904 | 0 | 0
3 | Fine planning at the bottom of the trench with accuracy of leveling ±2cm | m2 | 8.28 | 0 | 0
4 | Supply, transport and laying of sand with light compaction as base for the pipeline, d=10cm, around the pipe and above the pipe up to d=30cm | m3 | 3.933 | 0 | 0
5 | Supply, transport and layung pipes along with fittings and joint material into trench with dept of 1,10m
| PEHD pipes DN40 mm, PN 10 bari | m | 10.35 | 0 | 0
6 | Disinfection and hydraulics testing of water supply pipeline. | m | 10.35 | 0 | 0
7 | Backfilling the trench good material from excavation after finishing construction works, in 30cm layers with light compaction. | m3 | 3.519 | 0 | 0
8 | Loading, transport of excess material from excavation works to landflill at a distance of 5 km | m3 | 3.933 | 0 | 0
1.2. | Water meter shaft
1 | Excavation og earth material in III category of earth according to GN200 categorization, for water meter shaft at depth up to 2.0m' and depo the excavated material neat the trench. (the excavated material will be used for backfilling the trench. | m3 | 6.0603 | 0 | 0
2 | Suplly and laying concrete C25/30 for making the water meter shaft with its dimensions A/B/H=1.30/1.30/1.50, walls, base and cover plate d= 20сm.
| - base plate | m3 | 0.169 | 0 | 0
| - walls | m3 | 0.6994 | 0 | 0
| - cover plate | m3 | 0.075 | 0 | 0
3 | Supply, transport and installation of cast iron cover Ø500mm class C 250. | piece | 1 | 0 | 0
4 | Supply, transport and mounting reinfrocement for water meter shaft and steps at the shaft made form reinforcement RA 400/500-2 Ø20mm. | kg | 300 | 0 | 0
5 | Supply, transport and mounting of ductile iron fittings. Calculation per kg in specification into drawings -FFR piece Ø40/30mm Х 2 -FF piece Ø40мм, L=600mm X 2 -FF piece Ø40мм, L=400mm X 2 | kg | 48 | 0 | 0
6 | Supply and installation of reinforcing and shaped pieces in a water measuring shaft together with gaskets, screws and nuts
| Reducer 5/4'' на 1" | piece | 2 | 0 | 0
| Drain valve ф1'' | piece | 1 | 0 | 0
| Water meter Ø1" with a remote data reading system | piece | 1 | 0 | 0
| Non-return valve Ø1'' | piece | 1 | 0 | 0
7 | Backfilling the trench with good material from excavation after finishing constructuon works, in 30cm layerswith light compaction. | m3 | 3.5253 | 0 | 0
8 | Loading, transport of excess material from excavation works to landflill at a distance of 5 km | m3 | 2.535 | 0 | 0
1.3. | Internal plumbing
1 | Supply, transport and mounting of PPR pipes and fittings PN16 bar. The pipes should be according to German standards DIN 8078 and EN ISO 15874-2, also to posses certification for drinking water provided by macedonian institutions.
| OD 20 mm | m' | 99.245 | 0 | 0
| OD 25 mm | m' | 18.975 | 0 | 0
| OD 32 mm | m' | 5.405 | 0 | 0
2 | Supply and installation of galvanized pipes together with fittings. Led under the ceiling, in and along the wall with trimming slots and plastering
| Ф 5/4” | m' | 10.58 | 0 | 0
| Ф 1” | m' | 31.51 | 0 | 0
| Ф 3/4” | m' | 34.615 | 0 | 0
| Ф 1/2” | m' | 86.365 | 0 | 0
3 | Supply, transport and installation of thermal foam insulation for water pipes d=9 mm (halogen free) (cold water)
| Ф 5/4” | m' | 10.58 | 0 | 0
| Ф 1” | m' | 31.51 | 0 | 0
| Ф 3/4” | m' | 20.7 | 0 | 0
| Ф 1/2” | m' | 19.78 | 0 | 0
| OD 32 mm | m' | 5.405 | 0 | 0
| OD 25 mm | m' | 18.975 | 0 | 0
| OD 20 mm | m' | 38.525 | 0 | 0
4 | Supply, transport and installation of thermal sponge insulation for water pipes d=9 mm, with a conductivity not less than 0.04W/mK, with a vapor-impermeable membrane, fire-resistant (halogen free) (hot water and recirculation)
| Ф 3/4” - d=30mm | m' | 13.915 | 0 | 0
| Ф 1/2” - d=20mm | m' | 66.585 | 0 | 0
| OD 20 mm | m' | 60.72 | 0 | 0
5 | Supply and installation of through-valves with outlet on the verticals made according to EN 12288
| Ф 5/4 ” | piece | 1 | 0 | 0
6 | Supply and installation of brass valves made according to EN 12288
| Ф 1” | piece | 2 | 0 | 0
| Ф 3/4” | piece | 1 | 0 | 0
| Ф 1/2” | piece | 4 | 0 | 0
7 | Supply and installation of plastic polypropylene through-valves with a decorative cap according to ISO 15874-2
| OD 25 mm | piece | 1 | 0 | 0
| OD 20 mm | piece | 5 | 0 | 0
8 | Supply and installation of corner-Ek valves built into the wall with cap and rosette
| 1/2" | piece | 41 | 0 | 0
9 | Supply, transport and installation of clamps for fastening the distribution pipes | piece | 33 | 0 | 0
10 | Disinfection of the sanitary water supply network including examination of water quality in the pipes | m | 286.695 | 0 | 0
11 | Hydraulic testing of the sanitary water network according to the applicable regulations | m | 286.695 | 0 | 0
1.4. | Fire fighting water network
1 | Supply, transport and installation of fire fighting system from galvanized pipes:
| Ф 2 1/2” | m' | 30.25 | 0 | 0
| Ф 2” | m' | 11 | 0 | 0
2 | Supply, transport and installation of thermal foam insulation for fire fighting pipe network d=9 mm (halogen free)
| Ф 2 1/2” | m' | 30.25 | 0 | 0
| Ф 2” | m' | 11 | 0 | 0
3 | Supply, transport and installation of clamps for fastening the distribution pipes | piece | 8 | 0 | 0
4 | Supply and installation of FireHydrant 2" fire-fighting metal cabinets, complete with corner valve, rubberized hose l=15m, nozzle and wrench | piece | 4 | 0 | 0
5 | Hydraulic testing of the fire water supply network according to the applicable regulations | m | 41.25 | 0 | 0
6 | Testing of the fire fighting network by an authorized institution in order to obtain a certificate for its use. The price is given per tested hydrant. | piece | 4 | 0 | 0
2 | SEWAGE INSTALLATION
2.1. | FAECAL SEWAGE
2.1.1. | External fecal sewage (from the building to the first Fecal inspected shaft)
1 | Marking of route according to technical regulations for earthworks. | m' | 18.975 | 0 | 0
2 | Combined excavation, manual and machine, of earth material in III and IV category of earth according to GN200 categorization, for placing pipeline into trench with width up to 1.20m and depth 0-2.0m. Total V=15,18m3 from which:
| machine 80% | m3 | 12.144 | 0 | 0
| manual 20% | m3 | 3.036 | 0 | 0
3 | Fine planning at the bottom of the trench with accuracy of leveling ±2cm | m2 | 15.18 | 0 | 0
4 | Supply, transport and laying of sand with light compaction as base for the pipeline, d=10cm, around the pipe and above the pipe up to d=30cm | m3 | 7.2105 | 0 | 0
5 | Supply, transport and installation of corrugated PE sewer pipes SN 8, in accordance with EN13476-3 and street sewerage with hydraulic testing. |  |  | 0
| DN 160 mm | m | 18.975 | 0 | 0
6 | Backfilling the trench good material from excavation after finishing construction works, in 30cm layers with light compaction. | m3 | 7.9695 | 0 | 0
7 | Excavation for the expansion of the trench for shafts in category III ground with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 8.64 | 0 | 0
8 | Backfilling the space around the shaft with part of the excavated earth by compacting in layers | m3 | 1.728 | 0 | 0
9 | Removal of excess soil from excavation (from trench and from shaft) | m3 | 14.8815 | 0 | 0
10 | Supply and installation of concrete shafts with an average height of up to H=2.0 m with a cast iron cover D=160 kg for heavy traffic and dimensions according to the details given in the graphic section | piece | 3 | 0 | 0
2.1.2. | Internal SEWAGE
1 | Supply, transport and installation of PVC sewer pipes complete with fittings. Pipes should be according to the following standards: EN1451-1, EN13501-1 and stiffness class SN4. Long-term temperature resistance up to 95 ºC. Possibility of installation down to -10 ºC. Joint method with integrated joint and sealing ring (SBR). Brackets for vertical and horizontal anchoring should be included in the price.
| Ø100mm | m' | 89.705 | 0 | 0
| Ø70mm | m' | 37.455 | 0 | 0
| Ø50mm | m' | 21.615 | 0 | 0
2 | Supply, transport and installation of plastic polypropylene revisions, calculation per examined and installed piece.
| Ø 100 mm | piece | 6 | 0 | 0
3 | Supply, transport and installation of horizontal plastic polypropylene revisions, calculation per examined and installed piece.
| Ø 100 mm | piece | 2 | 0 | 0
4 | Supply, transportation and installation of a mounting box for the inspection of the sewage system placed in the hall. | piece | 2 | 0 | 0
5 | Machine wall boring through reinforced concrete slab for making a hole for sewage pipes | piece | 15 | 0 | 0
6 | Fill of the holes around newly positioned pipes with one component, self compacting mortar with cement base | piece | 15 | 0 | 0
7 | Making of polypropylene hole fillings for holes through walls and slabs where sewage pipe cross, according to EN 1366-3 | piece | 15 | 0 | 0
8 | Supply, transportation and installation of ventilation heads made of galvanized sheet
| Ø 150 | piece | 4 | 0 | 0
3 | SANITARY EQUIPMENT
1 | Supply, transport and installation of first class sanitary ceramics
| WC bowl with a low-mounting cistern, drain in the floor, complete with a toilet cover and connecting rubber | piece | 9 | 0 | 0
2 | Supply, transport and installation of first class sanitary ceramics
| Sink | piece | 9 | 0 | 0
| Nickel-plated sink siphon | piece | 9 | 0 | 0
| One-handed standing faucet with push mechanism for a sink with a drain mechanism for sanitary ceramics | piece | 9 | 0 | 0
3 | Supply, transport and installation of sinks with nickel-plated siphon | piece | 6 | 0 | 0
4 | Supply, transport and installation of plastic shower tubs, dimensions and color according to the Investor's choice | piece | 2 | 0 | 0
| - Shower faucet set | piece | 2 | 0 | 0
| - Plastic polypropylene vertical drain with nickel-plated grid Ø70mm | piece | 2 | 0 | 0
5 | Supply, transportation and installation of a 100l electric water heater in the toilets | piece | 1 | 0 | 0
6 | Supply, transportation and installation of a 10l electric water heater in the toilets | piece | 5 | 0 | 0
TOTAL WATER SUPPLY AND SEWAGE [MKD] |  |  |  |  | 0
VAT 18 % [MKD] |  |  |  |  | 0
TOTAL [MKD] |  |  |  |  | 0

## 05. SPRINKLER
BILL OF QUANTITY FOR SPRINKLER SYSTEM
No. | Description | Unit | Quantity | Unit Price (MKD) | Total Price (MKD)
1 | Supply, transport and installation of 2 FF electric pumps, 1 jockey pump with automation system, according to EN-12845 approved by FM, with steel substructure for connecting all elements, with the following technical specification: Pump manufactorr : SPP Pump model: KM08VM Pump capacity : 15 KW Pump type : Electric | piece | 1 | 0 | 0
2 | Supply, transport and installation of flow indicator: Manufactor: Tyco |  |  |  | 0
2.1 | DN 80 | piece | 2 | 0 | 0
3 | Supply, transport and installation of gate valve: Manufactor: Tyco |  |  |  | 0
3.1 | DN 150 | piece | 3 | 0 | 0
3.2 | DN 100 | piece | 2 | 0 | 0
4 | Supply, transport and installation of butterfly valve: Manufactor: Tyco |  |  |  | 0
4.1 | DN100 | piece | 4 | 0 | 0
4.2 | DN 80 | piece | 2 | 0 | 0
5 | Supply, transport and installation of micro switch for position control (open/closed) Manufactor: System sensor | piece | 11 | 0 | 0
6 | Fire Department Connections DN50 NST - B75 Manufactor: Giacomini | piece | 1 | 0 | 0
7 | Supply, transport and installation of check valve: Manufactor: Tyco |  |  |  | 0
7.1 | DN 100 | piece | 3 | 0 | 0
8 | Supply, transport and installation of test and drain valve DN 25, with K-factor: Manufactor: Giacomini |  |  |  | 0
8.1 | K80 | piece | 1 | 0 | 0
9 | Supply, transport and installation of drain valve DN 50 Manufactor: Giacomini | piece | 2 | 0 | 0
10 | Supply and transport of wrenches for installation of sprinkler nozzles | piece | 1 | 0 | 0
11 | Supply and transport of sprinkler head cabinet with 12 sprinkler pendent nozzles |  |  |  | 0
11.1 | K80 | piece | 1 | 0 | 0
12 | Supply, transport and installation of pressure gauge | piece | 5 | 0 | 0
13 | Supply, transport and installation of wet alarm valves , complete with all necessary parts : Wet Sprinkler valve- AV-1 Test and drain valve Alarm control valve Pressure gauge Test valve for the pressure gauge Pressure switch Manufactor: TYCO |  |  |  | 0
13.1 | DN 100 | piece | 1 | 0 | 0
14 | Supply, transport and installation of water motor alarm bell : Water Motor Support Washer Drive Shaft Drive Shaft Sleeve Gong Mount Striker See Gong Red Gong Repair Cap Nut WMA-1 Manufactor: Tyco | piece | 1 | 0 | 0
15 | Supply, transport and installation of pendent sprinkler nozzles 68° C, 1/2" white, QR Manufactor: Tyco |  |  |  | 0
15.1 | K80 | piece | 123 | 0 | 0
16 | Supply, transport and installation of ressete for pendent sprinkler nozzles 68° C, 1/2" white Manufactor: Tyco | piece | 123 | 0 | 0
17 | Supply, transport and installation of flexible hoses 3/4'' 1.2-1.8 m for suspended ceiling. FM approved. Manufactor: Ayvaz | piece | 123 | 0 | 0
18 | Supply, transport and installation of black steel pipes with grooved connections, complete with all connection material and painting (t-parts, joints, elbows etc.) FM approved, ASTM A795 factory painted with RAL3000 epoxy colour |  |  |  | 0
18.1 | DN 150 | m | 10 | 0 | 0
18.2 | DN 100 | m | 150 | 0 | 0
18.3 | DN 32 | m | 23 | 0 | 0
18.4 | DN 25 | m | 265 | 0 | 0
19 | Supply, transport and installation of pipe hengers, suports, threaded rod, nut e.t.c Manufactor: Erico |  |  |  | 0
19.1 | DN 100 | set | 51 | 0 | 0
19.2 | DN 32 | set | 6 | 0 | 0
19.3 | DN 25 | set | 96 | 0 | 0
20 | Supply, transport and installation of lateral seismic hagners, set. Manufactor: Erico |  |  |  | 0
20.1 | DN100 | set | 34 | 0 | 0
21 | Supply, transport and installation of longitudinal seismic hagners, set. Manufactor: Erico |  |  |  | 0
21.1 | DN100 | set | 28 | 0 | 0
22 | Supply, transport and installation of 4-way seismic hagners, set. Manufactor: Erico |  |  |  | 0
22.1 | DN100 | set | 4 | 0 | 0
23 | Distribution pipe DN150 with 2 outlets DN100 | piece | 1 | 0 | 0
24 | Supply, transport and installation of HDPE pipe PN16 with all elements needed to connect to the sprinkler tank (it does not include earthworks and concrete pours) |  |  |  | 0
24.1 | DN 150 | m | 11 | 0 | 0
25 | Supply, transport and installation of sprinkler addressabl fire control panel for the following signals: with installation input/output modul battery Pump run Pump error Sprinkler valve run Sprinkler tank level Open/ close position of gate valve with all electrical installation Manufactor :Siemens | piece | 1 | 0 | 0
26 | Testing and commissioning | lump sum | 1 | 0 | 0
27 | Supply, transport and installation of flow meter from 0-2000 l/min Manufactor: INFLUX | piece | 1 | 0 | 0
28 | Supply, transport and installation of "Antivortex" suction plate DN 150 | piece | 2 | 0 | 0
29 | Supply, transport and installation of pressure relief valve PN16 DN 150 Manufactor: Claval (FM approved) | piece | 2 | 0 | 0
30 | Supply, transport and installation of system for automatic control of water temperature and water level in the tank | lump sum | 1 | 0 | 0
TORAL WITHOUT VAT (MKD) : |  |  |  |  | 0
VAT 18% |  |  |  |  | 0
GRAND TOTAL: |  |  |  |  | 0

## 06. PHOTOVOLTAIC
Item No. | Description | Ref. | Unit | Unit Price [MKD] | Total Price [MKD]
1 | 2 | 3 | 4 | 5 | 6
BILL OF QUANTITIES AND CALCULATION
FOR THE EXECUTION OF ELECTRICAL INSTALLATIONS FOR A ADMINISTRATIVE BUILDING, WITHIN THE COMPLEX OF WHOLESALE TRADE OBJECTS – AGRIFOOD PLATFORM
PHOTOVOLTAIC PANELS FOR ELECTRICITY PRODUCTION WITH A MAXIMUM INSTALLED CAPACITY OF 57.67kW
NOTE:
* For all positions, procurement and delivery apply,
transportation, storage,installation and
connection, complete with minor auxiliary
material, ready for operation.
*For all the planned equipment
an equivalent shall apply.
1 | PHOTOVOLTAICS
1.1 | Supply, transportation and installation of monocrystalline photovoltaic panels with a power of 730Wp | piece | 79 | 0 | 0
1.2 | Three-phase free standing inverter with a power of 50kW | piece | 1 | 0 | 0
1.3 | Installation of new connections in the Main Distribution Board for the GRT-ADM.M facility with the following equipment: -Base for NH1 fuse switch disconnector, complete with isolator, 3-pole, quantity: 2 -Cartridge fuse with a rated current of 80A, NH3 type, quantity: 3 -Cartridge fuse with a rated current of 80A, NH3 type, quantity: 3 | piece | 1 | 0 | 0
1.4 | Solar cable: PV1-F 1 x 6mm². The cable is laid on perforated cable trays. There is a charge for a cable kit, cable ties, installation and electrical connection of the cables. | m | 420 | 0 | 0
1.5 | Power cable NYY-O 4x35mm2 + NYY-J 1x25mm2 for connecting Inverter with GRT-ADM.M | m | 25 | 0 | 0
1.6 | Power cable NYY-O 4x35mm2 + FeZn 30x4mm for connecting GRT-ADM.M to MRO | m | 100 | 0 | 0
1.7 | Protective cable: P/F 1x6mm2 yellow green color equipotential bonding between panels and lightning rod | m | 15 | 0 | 0
1.8 | Cable lugs for P/F 1x6mm2 for equipotential bonding | piece | 10 | 0 | 0
1.9 | Strip-cable conenctor for equipotential bonding of photovoltaic panels | piece | 10 | 0 | 0
1.10 | MC4+ connectors and pins for solar installations: | piece | 5 | 0 | 0
1.11 | MC4- connectors and pins for solar installations: | piece | 5 | 0 | 0
1.12 | UV stable hose F25-50mm for solar cable protection: PV1-F 1 x 6mm² from UV radiation, on parts where the cable is exposed to the sun and from potential mechanical damage. | m | 50 | 0 | 0
1.13 | Procurement, transport, and installation of a perforated cable tray 100x60mm, hot-dip galvanized in accordance with DIN EN ISO 1461:2009, with a length of L=3m for horizontal cable routing, complete with roof-mounted ladder supports placed every 1.5 to 2 meters, plugs, screws, and a cover along the entire length. The cable trays must be delivered with quick couplings; if not, grounding must be ensured, i.e., each 3m piece must be interconnected with the next using a P/F 1x6mm² conductor in yellow-green color. | piece | 17 | 0 | 0
| Total 1 |  |  |  | 0
2 | TECHNICAL DOCUMENTATION
2.1 | Puting into operation, testing and measuring of the installation by an accredited institution(company), including test protocol results for metering and the set of paremeters in accordance with the positive regulations for technical inspection for this ty | lump sum | 1 | 0 | 0
2.2 | Issuance of a certificate of compliance with regulations and standards | lump sum | 1 | 0 | 0
2.3 | Cleaning of the construction site from the works and materials produced during the installation of PV plant and its disposal in accordance with the environmental law, complete with included transportation. | lump sum | 1 | 0 | 0
| Total 2 |  |  |  | 0
SUMMARY:
1 | PHOTOVOLTAICS |  |  |  | 0
2 | TECHNICAL DOCUMENTATION |  |  |  | 0
TOTAL WITHOUT VAT: |  |  |  |  | 0
VAT 18%: |  |  |  |  | 0
TOTAL INCLUDING VAT: |  |  |  |  | 0

## 07. FP
Pos. | Description of works | Unit | Quantity | Price [MKD] | Total amount [MKD]
1 | Procurement and installation PP equipment (Type)
1.1 | Manual FP device type S-9 | piece | 10 | 0 | 0
1.2 | Manual FP device type CO 2 -5 | piece | 10 | 0 | 0
1.3 | Information boards: - In case of fire, call "193" | piece | 10 | 0 | 0
1.4 | Information boards: - Evacuation plan | piece | 10 | 0 | 0
1.5 | Signboards: Place for FP device | piece | 20 | 0 | 0
SUBTOTAL |  |  |  |  | 0
18% VAT |  |  |  |  | 0
TOTAL |  |  |  |  | 0

## RECAPITULATION
RECAPITULATION: ADMINISTRATIVE BUILDING
No. of pos. | Description of phase | Total Price [MKD]
1 | Architecture & Construction | 0
2 | Electrotechnics | 0
3 | Mechanical Installations | 0
4 | Hydrotechnics | 0
5 | Sprinkler | 0
6 | Photovoltaics | 0
7 | Fire Safety | 0
Subtotal |  | 0
18% VAT |  | 0
Grand total |  | 0