## WSS Site plan
1. PRE-MEASURE FOR A WELL SHAFT
Row no. | Description of the works | Unit of Measure | Quantity | Unit price (MKD) | Total (MKD)
1 | 2 | 3 | 4 | 5 | 6
1. WELL SHAFT
I. EARTHLY WORKS
1 | Combined excavation of earth III category in a wide excavation for a well shaft. Total: V= 48.00m3 from that:
| · manually 20% | m3 | 9.6 | 0 | 0
| · mechanical 80% | m3 | 38.4 | 0 | 0
2 | Gravel filling under the slab. Installation should be carried out with a vibrating plate in a layer of 20 cm. The upper surface is finely leveled to -/+2.0 cm.
| The calculation per m3 from laid material | m3 | 2.7 | 0 | 0
3 | Manual and mechanical piling of excavated soil around the shaft with compaction in layers of 20 cm. With a vibrating plate until the surrounding material is approximately compacted.
| Calculation per m3 | m3 | 22 | 0 | 0
4 | Removal of excess excavated material to a landfill
| the material at a distance of up to 5km. | m3 | 23 | 0 | 0
| TOTAL I: |  |  |  | 0
II. CONCRETE WORKS
1 | Making a layer under the foundation slab. The base should be made of unreinforced concrete MB 15 with a thickness of d=10.0cm. The concrete is placed over a layer of gravel d=20.0cm. Calculation per m3 | m3 | 1.3 | 0 | 0
2 | Production of reinforced concrete foundation slab d=25cm with waterproof concrete MB 30.
| Calculation per m3 | m3 | 3.2 | 0 | 0
3 | Construction of reinforced concrete walls d=25cm with waterproof concrete MB 30 in the required double-sided smooth formwork with the required vibration of the concrete.
| Calculation per m3 | m3 | 2.75 | 0 | 0
4 | Production of a reinforced concrete slab d=15cm. covered with concrete MB 30 in the required formwork.
| Calculation per m3 | m3 | 1 | 0 | 0
5 | Construction of concrete block support at T-piece of the well shaft thrust MB30. Calculation per m3 | m3 | 0.1 | 0 | 0
| TOTAL II: |  |  |  | 0
III. REINFORCEMENT WORKS
1 | Procurement, transportation, cleaning, cutting, bending and installation of reinforcement RA400/500-2 F <12. Calculation per 1 kg. of built-in reinforcement.
| ≤F12 | kg. | 1346 | 0 | 0
| ≥F12 | kg. | 133 | 0 | 0
| TOTAL III: |  |  |  | 0
IV. INSULATION WORKS
1 | Procurement, transportation and construction of horizontal and vertical waterproofing for protection against ground moisture with bitumen tape Bikutop with an overlap of 10 cm. | m2 | 43
| Calculation per m2 |  |  | 0 | 0
| TOTAL IV: |  |  |  | 0
V. PAINTING WORKS
1 | Painting of metal climbing frames with oil paint, previously sanded and cleaned, L=2.0m. | m' | 2 | 0 | 0
2 | Painting of ventilation metal pipe Ф200, L=2.0m. previously minimized and cleaned | piece | 1 | 0 | 0
| TOTAL V: |  |  |  | 0
VI. LOCKSMITH WORKS
1 | Installing a metal cover 1.1 with a key. | piece | 1 | 0 | 0
| Installation of metal interior climbing frames, calculation per piece | piece | 5 | 0 | 0
| Installation of ventilation pipe Ф200mm and ventilation cap Ф300mm., L=2.0m. With protective net | piece | 1 | 0 | 0
| TOTAL VI: |  |  |  | 0
VII. INSTALLATION WORKS
1 | Procurement, transportation and installation of cast iron fittings together with gaskets, bolts and nuts. Calculation per kg. according to specification in the drawing. | kg | 83 | 0 | 0
2 | Procurement, transportation and installation of PP adapter flanges with metal flange at the transition from polyethylene to cast iron. See specification. Calculation per piece.
| ND63 mm; PN 10 bar | piece | 1 | 0 | 0
3 | Procurement, transportation and installation of flat valves. Calculation per piece.
| f 65, NP 10 bar | piece | 1 | 0 | 0
4 | Procurement, transport and installation of a solenoid valve F 50, NP 10 bar. Calculation per piece. | piece | 1 | 0 | 0
5 | Procurement, transportation and installation of an automatic air valve. Calculation per piece. |  |  |  | 0
| DN 50, PN 10 bar | piece | 1 | 0 | 0
6 | Procurement, transport and installation of a filter ф65 mm. Calculation per piece. | piece | 1 | 0 | 0
7 | Procurement, transportation and installation of a non-return valve. Calculation per piece | piece | 1 | 0 | 0
8 | Procurement, transportation and installation of galvanized steel pipes Ф 63 mm PN 10bar with flanges FF 2000mm. Calculation per piece. | piece | 18 | 0 | 0
9 | Procurement, transportation and installation of a steel cable to hold the pump. Calculation per meter | m | 35 | 0 | 0
10 | Procurement, transportation and installation of a well pump together with a PM device and power cable. The pump selection is with the following parameters Q=2 l/s, H=35 m | piece | 1 | 0 | 0
11 | Procurement, transport and installation of PVC pipe Ф200mm L=1.5m. Intended for ventilation | m | 1.5 | 0 | 0
TOTAL VII: |  |  |  |  | 0
VIII. EXPLORATORY PUMPING WELL
1 | Preparatory works, excavation of basins, enabling technical water, and transportation costs | lump sum | 1 | 0 | 0
2 | Mechanical rotary drilling with water or percussion drilling up to 50 m, with a drilling diameter of Æ250 mm | m | 50 | 0 | 0
3 | Procurement, preparation, and installation of a well structure from solid and filter PVC pipes Ø140 mm, with factory line perforation 7.5%, with an opening width of 2 mm, 10 bar | m | 6 | 0 | 0
4 | Procurement and installation of a filter backfill around the well structure made of granular gravel of alluvial origin with a grain size of 4-8 mm from a final depth of up to 3 m below ground level | m3 | 6 | 0 | 0
5 | Procurement and installation of clay aggregate base at intervals of 0 - 3m | m | 3 | 0 | 0
6 | Cleaning and development of the well and the well area until clean water flows (with flushing and airlifting) | h | 12 | 0 | 0
7 | Well test with a step test, with continuous measurement of water quantities and groundwater level oscillations, with engineering supervision | h | 72 | 0 | 0
8 | Making a well cover with a concrete block with dimensions 0.6 x 0.6 x 0.3m | piece | 1 | 0 | 0
9 | Preparation of a complete physical-chemical, microbiological, radiological, parasitological analysis, and an analysis of pesticides in the water | analysis | 5 | 0 | 0
10 | Engineering supervision of the well construction | daily | 5 | 0 | 0
11 | Preparation of the Report in three copies | lump sum | 1 | 0 | 0
TOTAL VIII: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
2. RESERVOIR MEASUREMENT V = 100m3
I. PREPARATORY WORKS
1 | Geodetic marking of the location of the reservoir pit construction | m2 | 162 | 0 | 0
TOTAL I: |  |  |  |  | 0
II. EARTHWORKS
1 | Mechanical excavation of soil of category III and IV in a wide excavation for the installation of the reservoir. Total 700m3
| 20% manually | m3 | 280 | 0 | 0
| 80% machine-made | m3 | 420 | 0 | 0
2 | Rough and fine planning of the trench bottom | m2 | 129.6 | 0 | 0
3 | Loading and removal of excavated material up to 5 km away | m3 | 700 | 0 | 0
TOTAL II: |  |  |  |  | 0
III. CONCRETE WORKS
1 | Procurement, transportation and installation of concrete MB20, under the foundation slab at a height of 5 cm. | m2 | 60 | 0 | 0
2 | Procurement, transportation and installation of MB30 concrete, waterproofing additives in the 30 cm foundation slab in the wet chamber. | m3 | 12.9 | 0 | 0
3 | Procurement, transportation and installation of concrete MB30, waterproofing accessories in the 30 cm foundation slab in the dry chamber | m3 | 3.5 | 0 | 0
4 | Procurement, transportation and installation of MB30 concrete, with waterproofing additives in the external walls of the wet chamber with a thickness of 30 cm and a height of up to 3.75 m, with formwork and stripping of the one-sided planed formwork. | m3 | 26.77 | 0 | 0
5 | Procurement, transportation and installation of concrete MB30, with waterproofing additives in the internal partition wall in the wet chamber with a thickness of 20 cm and a height of 3.75 m. In the position, formwork and stripping of double-sided smooth formwork should be foreseen. | m3 | 6.41 | 0 | 0
6 | Procurement, transportation and installation of concrete MB 30, in the walls of the dry chamber with a thickness of 30 cm and a height of 4.05 m. In the position to foresee the formwork and removal of the double-sided smooth formwork. | m3 | 10.2 | 0 | 0
7 | Procurement, transportation and installation of concrete MB 30, in the roof slab d=20sm in the wet and dry chamber. In the position to be provided for supporting the formwork at a height of up to 3.75 m and removing the formwork. | m3 | 17.25 | 0 | 0
8 | Procurement, transportation and installation of cement mortar on the floor slab of the wet and dry chambers of the tank in a ratio of 1:2 on top of the waterproofing insulation with a slope of 2% with an average thickness of 7 cm | m2 | 55.75 | 0 | 0
9 | Procurement, transportation and installation of cement mortar on the roof slab of the wet and dry chamber, applied under waterproofing in a ratio of 1:2 on top of the waterproofing insulation with a slope of 2% with an average thickness of 7 cm. | m2 | 63 | 0 | 0
TOTAL III: |  |  |  |  | 0
IV. REINFORCEMENT WORKS
1 | Procurement, transportation, cleaning, cutting, bending and installation of reinforcement to be carried out according to the reinforcement plans and specification of the tank reinforcement. Calculation per 1 kg of installed reinforcement.
| ≤Ф12 | kg. | 7688 | 0 | 0
| ≥Ф12 | kg. | 668.7 | 0 | 0
TOTAL IV: |  |  |  |  | 0
V. LOCKSMITH WORKS
1 | Climbing frames made of galvanized metal box profiles 40/40 cm together with anchor plates embedded in the concreting phase in the walls with a length of 3300 m 1, a width of 300 mm and a depth of 150 mm. With steps placed 30 cm apart along the length. | piece | 3 | 0 | 0
2 | Procurement and installation of a cast iron rectangular cover with frame, dimensions 1.2 x 1.2 m, for heavy traffic. The cover shall be manufactured according to EN 124 (or equivalent standard), class D400. | piece | 1 | 0 | 0
TOTAL V: |  |  |  |  | 0
VI. INSULATION WORKS
1 | Waterproofing of external concrete surfaces exposed to underground influences. Waterproofing to be performed from bitumen tape Bikutop with an overlap of 10 cm. | m2 | 305 | 0 | 0
2 | Protection of external waterproofing from mechanical damage with a high-density polyethylene membrane HDPE TIP telephone number with semicircular protrusions of 8 mm with lateral joining of the material (Together with all connecting elements for quality installation of insulation) | m2 | 305 | 0 | 0
3 | Coating the walls from the inside of the floor slab, the ceiling with a cement-based insulating coating in three layers with a brush or trowel. Calculation per m2 | m2 | 230 | 0 | 0
TOTAL VI: |  |  |  |  | 0
VII. INSTALLATION WORKS
1 | Procurement, transportation and installation of reinforcement fittings together with gaskets, screws and nuts. Calculation per kg. | kg. | 1046.5 | 0 | 0
2 | Procurement, transportation and installation of adapter flange for transition from polyethylene to cast iron.
| -Adapter flange ND 63 mm | piece | 3 | 0 | 0
| - Adapter flange ND 110 mm | piece | 1 | 0 | 0
3 | Procurement, transportation and installation of OZ valve. Calculation per piece.
| OZ valve Æ 50mm | piece | 2 | 0 | 0
4 | Procurement, transportation and installation of OZ valve. Calculation per piece.
| OZ valve Æ 50mm | piece | 2 | 0 | 0
5 | Procurement, transport and installation of a float valve. Calculation per piece. | piece | 1 | 0 | 0
6 | Procurement, transport and installation of an electromotor valve. EMV F 80mm Complete with automation, and reporting to the PP control center. Calculation per piece. | piece | 1 | 0 | 0
7 | Procurement, transportation and installation of Suction basket without valve. Calculation per piece. | piece | 1 | 0 | 0
8 | Procurement, transportation and installation of a drainage pump: UNILIFT AP50B.50.11.A1V 1X230V 10M SCH. (REFERENCE PRODUCT) TYPE: N=1.30KW, Q=5.7l/s, H=7m Calculation per piece. | piece | 1 | 0 | 0
9 | Procurement, transportation and installation of a pump for draining technical water. HYDRO EN 32-200/200 S2JSADL-U1, according to standard EN 12845 (REFERENCE PRODUCT): Q=10 l/s, H=43m Calculation per piece. The price includes the test line, suction and commissioning of the pump. | piece | 1 | 0 | 0
10 | Procurement, transportation and installation of a pump for draining irrigation water. CMBE 5-62 IUCC--DB, according to standard EN 12845 (REFERENCE PRODUCT): Q=1.5 l/s, H=17m Calculation per piece | piece | 1 | 0 | 0
11 | Procurement, transportation and installation of ventilation made of shaped pieces of hard polyethylene
| Ventilation steel pipe with cap Ø150mm L= 1000mm | piece | 1 | 0 | 0
| Adapter flange ND160 mm | piece | 1 | 0 | 0
| Ventilation pipe with connection Pe -100 ND 160mm L= 1000mm | piece | 1 | 0 | 0
Together with the flange, it is made of steel pipe, anti-corrosion protected, oil-painted twice.
TOTAL VII: |  |  |  |  | 0
VIII. DRAINAGE
1 | Manual excavation of soil to form a channel with manual removal of the excavated material outside the construction pit. | m3 | 5.12 | 0 | 0
2 | Procurement, transportation and installation of MB20 concrete in the drainage base | m3 | 5.12 | 0 | 0
3 | Procurement, transportation and installation of PE drainage pipes ND 110mm L=20m together with elbows (4 pieces) | m | 34.12 | 0 | 0
4 | Procurement, transportation and installation of granulated gravel along the length of the drainage pipe with a grain size of 1-4 mm | m3 | 6.82 | 0 | 0
5 | Making openings during the concreting phase at the entrance of the branches of the drainage from the dry chamber. | piece | 2 | 0 | 0
TOTAL VIII: |  |  |  |  | 0
IX. MISCELLANEOUS MATTERS
1 | Interior cleaning of wall, floor and ceiling surfaces, washing with pressure water and disinfection with chlorine solution in accordance with regulations. | lump sum | 1 | 0 | 0
TOTAL IX: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
3. External water supply network
Sanitary, fire and technical water for the facility
1.1 | Tank for sanitary water W=25m3
1 | Earthworks
1 | Planning the terrain along with marking the facility | m2 | 21 | 0 | 0
2 | Extensive mechanical excavation of soil of category III and IV | m3 | 72 | 0 | 0
3 | Backfilling with compaction of gravel d=20.0cm | m3 | 4.8 | 0 | 0
4 | Backfilling by compacting the excavated soil around the object in layers of 20-30cm | m3 | 65 | 0 | 0
5 | Loading and transporting the remaining excavated soil by truck to a designated landfill | m3 | 7 | 0 | 0
2 | Concrete and reinforced concrete works
1 | Concreting of reinforced concrete slab d=30.0cm MB-30 | m3 | 6.3 | 0 | 0
2 | Laying a layer of lean concrete d=10cm | m3 | 2.1 | 0 | 0
3 | Reinforcement works
1 | Procurement, cutting and installation of RA-400/500 up to f8-12
| Bars f8 | kg. | 250 | 0 | 0
4 | Tank for sanitary water
1 | Procurement and installation of a tank made of ribbed polyethylene material Dowlex 2432, for a volume of 25m3 | piece | 1 | 0 | 0
Total 1.1.: |  |  |  |  | 0
1.2 | Pumping station for sanitary water
1 | Excavation of category III soil in a trench for a connection shaft to a depth of up to 1.2m with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 22 | 0 | 0
2 | Leveling and preparing the bottom for a foundation slab | m2 | 5.7 | 0 | 0
3 | Procurement and installation of concrete MB 30 for the water meter shaft with external dimensions A/B/H=2.6/2.2/3.0, for walls, floor and roof slab with a thickness of 20cm
| - floor slab | m3 | 1.15 | 0 | 0
| - walls | m3 | 6.2 | 0 | 0
| - roof slab | m3 | 0.95 | 0 | 0
4 | Procurement and installation of a cast iron rectangular cover with frame, dimensions 1.0 x 1.0 m, for heavy traffic. The cover shall be manufactured according to EN 124 (or equivalent standard), class D400. | piece | 1 | 0 | 0
5 | Procurement and installation of reinforcement together with climbing frames | kg | 610 | 0 | 0
6 | Coating the walls on the inside of the shaft with a cement-based insulating coating, two-component waterproofing. Calculation per m2 | m2 | 27 | 0 | 0
7 | Waterproofing of external concrete surfaces exposed to underground influences. Waterproofing to be performed from bitumen tape Bikutop with an overlap of 10 cm. | m2 | 23 | 0 | 0
8 | Protection of external waterproofing from mechanical damage with a high-density polyethylene membrane HDPE TIP telephone numberwith semicircular protrusions of 8 mm with lateral joining of the material (Together with all connecting elements for quality installation of insulation) | m2 | 33 | 0 | 0
9 | Backfilling the trench with excavated soil in layers with compaction of soil and gravel | m3 | 12 | 0 | 0
10 | Procurement, transportation and installation of reinforcement fittings together with gaskets, screws and nuts. Calculation per kg. | kg | 98.5 | 0 | 0
11 | Procurement, transportation and installation of adapter flange for transition from polyethylene to cast iron.
| -Adapter flange ND 63 mm | piece | 1 | 0 | 0
| -Adapter flange ND 90 mm | piece | 1 | 0 | 0
12 | Procurement, transportation and installation of PZ valve Ф50mm. Calculation per piece. | piece | 1 | 0 | 0
13 | Removal of excess material from excavation to a landfill at a distance of 5km | m3 | 12 | 0 | 0
14 | Procurement, transportation and installation of a sanitary water drainage pump. HYDRO MULTI-E 2CME 10-2 adopted according to standard EN 12845 (REFERENCE PRODUCT): Q=6 l/s, H=38m, Calculation per piece | piece | 1 | 0 | 0
Total 1.2.: |  |  |  |  | 0
1.3 | Design and implementation of filter station with equipement
1 | Design and implementtaion of a filter station including procurement, transportation and installation of equipment for water purification from a well. (This project documentation will be developed in accordance with the analysis of the water from the water well.) | piece | 1 | 0 | 0
Total 1.3.: |  |  |  |  | 0
1.4. | External network for sanitary water and fire hydrant network
1. | Marking the route of an excavation trench | m' | 905 | 0 | 0
2 | Mechanical excavation of earth, category III, in a trench with a width of 1.0 m and a depth of up to 1.20 m, with disposal of the excavated material next to the trench (part to be used for backfilling) (The pipes for the hydrant network and sanitary water are laid in the same trench, as well as the irrigation pipeline from JP2-JP14, with a length of 285 m, is laid in the same trench)) V=1004.2m3
| manually 20% | m3 | 200.84 | 0 | 0
| mechanical 80% | m3 | 803.36 | 0 | 0
3. | Bottom planning accuracy + -2sm | m2 | 708 | 0 | 0
4. | Procurement and spreading of sand along the bottom of the trench in a layer of 10 cm and approximately 30 cm above the pipe | m3 | 450.6 | 0 | 0
5 | Procurement and installation of pipes together with fittings and joint material at a depth of 1.00m
| PEHD pipes DN32mm, PN 10 bari | m | 370 | 0 | 0
| PEHD pipes DN40 mm, PN 10 bari | m | 233 | 0 | 0
| PEHD pipes DN50 mm, PN 10 bari | m | 175 | 0 | 0
| PEHD pipes DN63mm, PN 10 bari | m | 306 | 0 | 0
| PEHD pipes DN90 mm, PN 10 bari | m | 20 | 0 | 0
| PEHD pipes DN110 mm, PN 10 bari | m | 885 | 0 | 0
6 | Disinfection and hydraulic testing of (the entire network) | m | 1990 | 0 | 0
7 | Backfilling the trench with excavated soil in layers of 30 cm with compaction | m3 | 553.4 | 0 | 0
8 | Removal of excess material from excavation to a landfill at a distance of 5km | m3 | 450.6 | 0 | 0
9 | Procurement and installation of an underground fire hydrant PH80/750 mm, complete with a PZ valve Ф80 mm with cap and installation set, oval hydrant cap and connecting material | piece | 14 | 0 | 0
10 | Procurement and installation of reinforcement and fittings for an underground fire hydrant, including gaskets, screws and nuts
| -AF Ø110mm | piece | 28 | 0 | 0
| -T Ø110/80mm | piece | 14 | 0 | 0
| -FF Ø80mm L=200mm | piece | 14 | 0 | 0
| -N Ø80mm | piece | 14 | 0 | 0
Total 1.4.: |  |  |  |  | 0
1.5. | External irrigation network
1. | Marking the route of an excavation trench | m' | 400 | 0 | 0
2 | Mechanical excavation of category III earth in a trench with a width of 0.6 m and a depth of up to 0.80 m, with disposal of the excavated material next to the trench (part to be used for backfilling)V=256m3
| manually 20% | m3 | 51.2 | 0 | 0
| mechanical 80% | m3 | 204.8 | 0 | 0
3. | Bottom planning accuracy + -2sm | m2 | 684 | 0 | 0
4. | Procurement and spreading of sand along the bottom of the trench in a layer of 10 cm and approximately 30 cm above the pipe | m3 | 72 | 0 | 0
5 | Procurement and installation of pipes together with fittings and joint material at a depth of 0.80m
| PEHD pipes DN32mm, PN 10 bari | m | 370 | 0 | 0
| PEHD pipes DN63mm, PN 10 bari | m | 30 | 0 | 0
6 | Disinfection and hydraulic testing of (the entire network) | lump sum | 400 | 0 | 0
7 | Backfilling the trench with excavated soil in layers of 30 cm with compaction | m3 | 184 | 0 | 0
8 | Removal of excess material from excavation to a landfill at a distance of 5km | m3 | 72 | 0 | 0
9 | Procurement and installation of a garden hydrant f 1 '' complete with a cast iron oval cap. Calculation per installed piece. | piece | 18 | 0 | 0
Total 1.5.: |  |  |  |  | 0
1.6. | Connection shaft for technical water for irrigation network
1 | Excavation of category III soil in a trench for a connection shaft to a depth of up to 1.2m with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 2 | 0 | 0
2 | Procurement and installation of concrete MB 30 for the water meter shaft with external dimensions A/B/H=1.10/1.10/1.2, for walls, floor and roof slab with a thickness of 15cm
| - floor slab | m3 | 0.15 | 0 | 0
| - walls | m3 | 0.72 | 0 | 0
| - roof slab | m3 | 0.15 | 0 | 0
3 | Procurement and installation of a cast iron rectangular cover 600mm | piece | 1 | 0 | 0
4 | Procurement and installation of concrete reinforcement and climbing frames | piece | 3 | 0 | 0
5 | Procurement and installation of reinforcement and fittings in the connection shaft, together with gaskets, screws and nuts
| -AF Ø63mm | piece | 2 | 0 | 0
| -FF piece Ø50mm, L=600mm X 1 | piece | 2 | 0 | 0
| -T piece Ø50/50mm, L=600mm X 1 | piece | 1 | 0 | 0
| -OZ Ø63mm with wheel | piece | 1 | 0 | 0
6 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 1 | 0 | 0
7 | Removal of excess soil from excavation to a landfill at a distance of 5.0km | m3 | 1 | 0 | 0
Total 1.6.: |  |  |  |  | 0
1.7. | Technical water supply network for sprinkler system
1. | Marking the route of an excavation trench | m' | 160 | 0 | 0
2 | Mechanical excavation of earth, category III, in a trench with a width of 0.8 m and a depth of up to 1.20 m, with disposal of the excavated material next to the trenchV=100m3
| manually 20% | m3 | 20 | 0 | 0
| mechanical 80% | m3 | 80 | 0 | 0
3. | Bottom planning accuracy + -2sm | m2 | 128 | 0 | 0
4. | Procurement and spreading of sand along the bottom of the trench in a layer of 10 cm and approximately 30 cm above the pipe | m3 | 64 | 0 | 0
5 | Procurement and installation of pipes together with fittings and joint material at a depth of 1.20m
| PEHD pipes DN63mm, PN 10 bari | m | 160 | 0 | 0
6 | Backfilling the trench with excavated soil in layers of 30 cm with compaction | m3 | 36 | 0 | 0
7 | Removal of excess material from excavation to a landfill at a distance of 5km | m3 | 4.8 | 0 | 0
Total 1.7: |  |  |  |  | 0
1.8. | Water supply pipeline from a well
1. | Marking the route of an excavation trench | m' | 15 | 0 | 0
2 | Mechanical excavation of earth, category III, in a trench with a width of 0.8 m and a depth of up to 1.20 m, with disposal of the excavated material next to the trenchV=20m3
| manually 20% | m3 | 4 | 0 | 0
| mechanical 80% | m3 | 16 | 0 | 0
3. | Bottom planning accuracy + -2sm | m2 | 12 | 0 | 0
4. | Procurement and spreading of sand along the bottom of the trench in a layer of 10 cm and approximately 30 cm above the pipe | m3 | 4.8 | 0 | 0
5 | Procurement and installation of pipes together with fittings and joint material at a depth of 1.20m
| PEHD pipes DN63mm, PN 10 bari | m | 30 | 0 | 0
6 | Backfilling the trench with excavated soil in layers of 30 cm with compaction | m3 | 9.6 | 0 | 0
7 | Removal of excess material from excavation to a landfill at a distance of 5km | m3 | 4.8 | 0 | 0
Total 1.8: |  |  |  |  | 0
1.9. | Overflow pipeline from a tank
1. | Marking the route of an excavation trench | m' | 10 | 0 | 0
2 | Mechanical excavation of earth, category III, in a trench with a width of 0.8 m and a depth of up to 1.20 m, with disposal of the excavated material next to the trenchV=5.76m3
| manually 20% | m3 | 1.152 | 0 | 0
| mechanical 80% | m3 | 4.608 | 0 | 0
3. | Bottom planning accuracy + -2sm | m2 | 4.8 | 0 | 0
4. | Procurement and spreading of sand along the bottom of the trench in a layer of 10 cm and approximately 30 cm above the pipe | m3 | 1.92 | 0 | 0
5 | Procurement and installation of pipes together with fittings and joint material at a depth of 1.20m
| PEHD pipes DN150mm, PN 10 bari | m | 10 | 0 | 0
6 | Backfilling the trench with excavated soil in layers of 30 cm with compaction | m3 | 3.84 | 0 | 0
7 | Removal of excess material from excavation to a landfill at a distance of 5km | m3 | 1.92 | 0 | 0
Total 1.9.: |  |  |  |  | 0
1.10. | Drained pipeline from tank
1. | Marking the route of an excavation trench | m' | 10 | 0 | 0
2 | Mechanical excavation of earth, category III, in a trench with a width of 0.8 m and a depth of up to 1.20 m, with disposal of the excavated material next to the trenchV=5.76m3
| manually 20% | m3 | 1.152 | 0 | 0
| mechanical 80% | m3 | 4.608 | 0 | 0
3. | Bottom planning accuracy + -2sm | m2 | 4.8 | 0 | 0
4. | Procurement and spreading of sand along the bottom of the trench in a layer of 10 cm and approximately 30 cm above the pipe | m3 | 1.92 | 0 | 0
5 | Procurement and installation of pipes together with fittings and joint material at a depth of 1.20m
| PEHD pipes DN 63mm, PN 10 bari | m | 10 | 0 | 0
6 | Backfilling the trench with excavated soil in layers of 30 cm with compaction | m3 | 3.84 | 0 | 0
7 | Removal of excess material from excavation to a landfill at a distance of 5km | m3 | 1.92 | 0 | 0
Total 1.10.: |  |  |  |  | 0
All Total: |  |  |  |  | 0
4. External sewage system
4.1 Branch 1 -section FRS 1-FRS 9,sectionFRS 15-FRS 3,section FRS 36-Outlet
I GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 262.9 | 0 | 0
TOTAL I: |  |  |  |  | 0
II EARTHLY WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 470.7m3 of which:
| Mechanical excavation 80% | m3 | 376.56 | 0 | 0
| Manual excavation 20% | m3 | 94.14 | 0 | 0
2 | Excavation of a trench with a depth of 2 - 4 m and a width of 1.5 m for laying sewer pipes in soil of category III/IV according to the GN200 soil categorization. Calculation per m3.
| Mechanical excavation 80% | m3 | 63.2 | 0 | 0
| Manual excavation 20% | m3 | 15.8 | 0 | 0
3 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 236.61 | 0 | 0
4 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 113.95 | 0 | 0
6 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 480.75 | 0 | 0
7 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 160 mm | m | 62.72 | 0 | 0
| DN 200 mm | m | 200 | 0 | 0
| DN 250 mm | m | 30 | 0 | 0
8 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 64 | 0 | 0
9 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 32 | 0 | 0
10 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 145.95 | 0 | 0
11 | Procurement, transport and installation of reinforced concrete sewer inspection and inspection-cascade manholes with a diameter of ID1000 mm, which are composed of elements (cone, extension and bottom). The price includes the installation of metal climbing frames in the manhole. The manholes must have a reinforced concrete ring to accept vertical loads. The manhole cover must be cast iron, heavy type (400 kg). The calculation includes excavation and removal of excess soil to a landfill located up to L= 5 km away.
| 1.5 - 2.0 m | piece | 2 | 0 | 0
| 2.0 - 2.5 m | piece | 5 | 0 | 0
| 2.5 - 3.0 m | piece | 3 | 0 | 0
12 | Procurement and installation of reinforced concrete manholes (monoliths) with a clear opening of 600 mm with a wall and slab thickness of 20 cm, average manhole height up to H=1.0 m with a cast iron cover D=160 kg for heavy traffic and dimensions according to the details given in the graphic section. The manhole is installed after the WWTP | piece | 1 | 0 | 0
TOTAL II: |  |  |  |  | 0
III. DISCHARGE INTO A CANAL
1. ASSEMBLY WORKS
1 | Procurement, transportation and installation of a frog cover for the outlet of purified water. Calculation per piece. DN 250 mm | piece | 1 | 0 | 0
TOTAL: |  |  |  |  | 0
2. CONCRETE WORKS
1 | Procurement, transportation and installation of reinforced concrete C30/37 for the construction of a drain. | m3 | 2.56 | 0 | 0
2 | Procurement, transportation and installation of lean concrete C12/15 as a base for installing the drain. | m3 | 0.7 | 0 | 0
TOTAL : |  |  |  |  | 0
3. REINFORCEMENT WORKS
1 | Procurement, transportation and installation of B500B reinforcement according to technical specifications. | kg | 275 | 0 | 0
TOTAL : |  |  |  |  | 0
TOTAL III: |  |  |  |  | 0
IV. | WATER TREATMENT PLANT
1 | Earthworks
1 | Planning the terrain along with marking the facility | m2 | 45.76 | 0 | 0
2 | Extensive mechanical excavation of soil of category III and IV | m3 | 217.008 | 0 | 0
3 | Backfilling with compaction of gravel d=20.0cm | m3 | 6.392 | 0 | 0
4 | Backfilling by compacting the excavated soil around the object in layers of 20-30cm | m3 | 167.4786 | 0 | 0
5 | Loading and transporting the remaining excavated soil by truck to a designated landfill | m3 | 49.5294 | 0 | 0
2 | Concrete and reinforced concrete works
1 | Concreting of reinforced concrete slab d=30.0cm MB-30 | m3 | 14.4 | 0 | 0
2 | Laying a layer of lean concrete d=10cm | m3 | 4.8 | 0 | 0
3 | Reinforcement works
1 | Procurement, cutting and installation of RA-400/500 up to f8-12
| Bars f8 | kg. | 311.04 | 0 | 0
4 | Water treatment plant
1 | Procurement and installation of a ROClean 200PE treatment plant V=50m3 | piece | 1 | 0 | 0
2 | Procurement, transportation and installation of a chemical air filter | piece | 1 | 0 | 0
TOTAL IV: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
4.2 Sewage network Branch 2-Poteg FRŠ 10-FRŠ 2
I GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 129.05 | 0 | 0
TOTAL I: |  |  |  |  | 0
II EARTHLY WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 129.05m3 of which:
| Mechanical excavation 80% | m3 | 103.272 | 0 | 0
| Manual excavation 20% | m3 | 25.818 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 103.24 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 49 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 80.05 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing. |  |  | 0
| DN 160 mm | m | 90.48 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 30 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 15 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 64 | 0 | 0
9 | Procurement, transport and installation of reinforced concrete sewer inspection and inspection-cascade manholes with a diameter of ID1000 mm, which are composed of elements (cone, extension and bottom). The price includes the installation of metal climbing frames in the manhole. The manholes must have a reinforced concrete ring to accept vertical loads. The manhole cover must be cast iron, heavy type (400 kg). The calculation includes excavation and removal of excess soil to a landfill located up to L= 5 km away.
| 1.0 - 1.5 m | piece | 2 | 0 | 0
| 1.5 - 2.0 m | piece | 3 | 0 | 0
TOTAL II: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
4.3 Sewerage network Branch 3 - Section FRS 21-FRS 2
I GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 298 | 0 | 0
TOTAL I: |  |  |  |  | 0
II EARTHLY WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 468.44m3 of which:
| Mechanical excavation 80% | m3 | 374.752 | 0 | 0
| Manual excavation 20% | m3 | 93.688 | 0 | 0
2 | Excavation of a trench with a depth of 2 - 4 m and a width of 1.5 m for laying sewer pipes in soil of category III/IV according to the GN200 soil categorization. Calculation per m3.
| Mechanical excavation 80% | m3 | 13.648 | 0 | 0
| Manual excavation 20% | m3 | 3.412 | 0 | 0
3 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 238.4 | 0 | 0
4 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 163.48 | 0 | 0
5 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 322.03 | 0 | 0
6 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 160 mm | m | 180.93 | 0 | 0
| DN 200 mm | m | 117.05 | 0 | 0
7 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 57.6 | 0 | 0
8 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 28.8 | 0 | 0
9 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 192.28 | 0 | 0
10 | Procurement, transport and installation of reinforced concrete sewer inspection and inspection-cascade manholes with a diameter of ID1000 mm, which are composed of elements (cone, extension and bottom). The price includes the installation of metal climbing frames in the manhole. The manholes must have a reinforced concrete ring to accept vertical loads. The manhole cover must be cast iron, heavy type (400 kg). The calculation includes excavation and removal of excess soil to a landfill located up to L= 5 km away.
| 1.0 - 1.5 m | piece | 2 | 0 | 0
| 1.5 - 2.0 m | piece | 4 | 0 | 0
| 2.0 - 2.5 m | piece | 4 | 0 | 0
TOTAL II: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
4.4 Sewage network Branch 4-Section FRŠ 29-FRŠ 7
I GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 74.62 | 0 | 0
TOTAL I: |  |  |  |  | 0
II EARTHLY WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 109.56m3 of which:
| Mechanical excavation 80% | m3 | 87.648 | 0 | 0
| Manual excavation 20% | m3 | 21.912 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 59.696 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 34.31 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 75.25 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing. |  |  | 0
| DN 160 mm | m | 74.62 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 18 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 9 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 43.31 | 0 | 0
9 | Procurement, transport and installation of reinforced concrete sewer inspection and inspection-cascade manholes with a diameter of ID1000 mm, which are composed of elements (cone, extension and bottom). The price includes the installation of metal climbing frames in the manhole. The manholes must have a reinforced concrete ring to accept vertical loads. The manhole cover must be cast iron, heavy type (400 kg). The calculation includes excavation and removal of excess soil to a landfill located up to L= 5 km away.
| 1.5 - 2.0 m | piece | 3 | 0 | 0
TOTAL II: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
4.5 Sewage network Branch 5-Section FRŠ 26-FRŠ 21
I GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 48.37 | 0 | 0
TOTAL I: |  |  |  |  | 0
II EARTHLY WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 63.96m3 of which:
| Mechanical excavation 80% | m3 | 51.168 | 0 | 0
| Manual excavation 20% | m3 | 12.792 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 38.696 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 19.57 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 44.39 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 160 mm | m | 48.37 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 15.6 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 7.8 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 27.37 | 0 | 0
9 | Procurement, transport and installation of reinforced concrete sewer inspection and inspection-cascade manholes with a diameter of ID1000 mm, which are composed of elements (cone, extension and bottom). The price includes the installation of metal climbing frames in the manhole. The manholes must have a reinforced concrete ring to accept vertical loads. The manhole cover must be cast iron, heavy type (400 kg). The calculation includes excavation and removal of excess soil to a landfill located up to L= 5 km away.
| 1.0 - 1.5m | piece | 2 | 0 | 0
| 1.5 - 2.0 m | piece | 1 | 0 | 0
TOTAL II: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
4.6 Sewage network Branch 6-Section FRŠ 32-FRŠ 7
I GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 42.83 | 0 | 0
TOTAL I: |  |  |  |  | 0
II EARTHLY WORKS
1 | Excavation of a trench with a depth of 0 - 2 m and a width of 1.0 m for laying sewer pipes in soil category III/IV according to the GN200 soil categorization. Calculation per m3.
| Mechanical excavation 80% | m3 | 50.96 | 0 | 0
| Manual excavation 20% | m3 | 12.74 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 34.264 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 20.55 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 43.15 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 160 mm | m | 42.83 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 15.6 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 7.8 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 28.35 | 0 | 0
9 | Procurement, transport and installation of reinforced concrete sewer inspection and inspection-cascade manholes with a diameter of ID1000 mm, which are composed of elements (cone, extension and bottom). The price includes the installation of metal climbing frames in the manhole. The manholes must have a reinforced concrete ring to accept vertical loads. The manhole cover must be cast iron, heavy type (400 kg). The calculation includes excavation and removal of excess soil to a landfill located up to L= 5 km away.
| 1.0 - 1.5m | piece | 2 | 0 | 0
| 1.5 - 2.0 m | piece | 1 | 0 | 0
TOTAL II: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
5. External storm sewer network
5.1 Storm water sewer Branch 1 Section ARSH1 - Outlet 1
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 450.49 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 716.60m3 of which:
| Mechanical excavation 80% | m3 | 573.28 | 0 | 0
| Manual excavation 20% | m3 | 143.32 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 450.49 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 154.27 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 562.33 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 315 mm | m | 217.65 | 0 | 0
| DN 400 mm | m | 111.12 | 0 | 0
| DN 500 mm | m | 121.72 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 88.4 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 44.2 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 198.47 | 0 | 0
9 | Procurement, transport and installation of reinforced concrete sewer inspection and inspection-cascade manholes with a diameter of ID1000 mm, which are composed of elements (cone, extension and bottom). The price includes the installation of metal climbing frames in the manhole. The manholes must have a reinforced concrete ring to accept vertical loads. The manhole cover must be cast iron, heavy type (400 kg). The calculation includes excavation and removal of excess soil to a landfill located up to L= 5 km away.
| 1.0 - 1.5m | piece | 11 | 0 | 0
| 1.5 - 2.0 m | piece | 6 | 0 | 0
10 | Procurement, transportation and installation of an oil separator with a capacity of Qmax = 200 l/s, with a 10% bypass. The separator shall be supplied with a coalescent filter, an inspection area and sampling for testing the treated water. The price shall also include inspection covers for the separator. | piece | 1 | 0 | 0
TOTAL II: |  |  |  |  | 0
3.DISCHARGE INTO A CANAL
3.1 ASSEMBLY WORKS
1 | Procurement, transportation and installation of a frog cover on the outlet of the storm sewer. Calculation per piece. DN 500 mm | piece | 1 | 0 | 0
TOTAL: |  |  |  |  | 0
3.2 CONCRETE WORKS
1 | Procurement, transportation and installation of reinforced concrete C30/37 for the construction of a drain. | m3 | 2.56 | 0 | 0
2 | Procurement, transportation and installation of lean concrete C12/15 as a base for installing the drain. | m3 | 0.7 | 0 | 0
TOTAL : |  |  |  |  | 0
3.3 REINFORCEMENT WORKS
1 | Procurement, transportation and installation of B500B reinforcement according to technical specifications. | kg | 275 | 0 | 0
TOTAL : |  |  |  |  | 0
TOTAL III: |  |  |  |  | 0
4. CONNECTION OF DRAINS AND GRIDS FOR ATM. SEWERAGE
1 | Excavation of soil of category III and IV for a trench, with a width of 0.8m and a depth of 0-2.0m, total V = 365 m3 of which:
| mechanical 80% | m3 | 292 | 0 | 0
| manual 20% | m3 | 73 | 0 | 0
2 | Bottom planning accuracy + -2sm | m2 | 104 | 0 | 0
3 | Procurement and spreading of sand along the bottom of the trench to a thickness of 10cm. | m3 | 30.4 | 0 | 0
4 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 160 mm | m' | 260 | 0 | 0
| DN 200 mm | m' | 130 | 0 | 0
5 | Backfilling the trench in layers up to 30 cm above the top of the pipe with sand, by manual compaction. | m3 | 140 | 0 | 0
6 | Backfilling the trench in layers of 30cm with gravelly sandy material from the site (natural or crushed stone), with manual or mechanical compaction. | m3 | 194.6 | 0 | 0
7 | Construction of a street drain for storm water on a concrete base d=15cm together with a cast iron grate min. 500x500 straight shape, construction height min. 150 mm, external dimensions of the frame min. 500 x 500 mm. Load class min. D 400 according to EN124. (or equivalent) | piece | 20 | 0 | 0
8 | Procurement, transport and installation of a linear drainage channel made of polymer concrete, with dimensions L=100 cm, B=19cm; H=21 cm; galvanized steel edge, complete with cast grating with load class D400 in accordance with EN 1433. The price should also include end plates. | piece | 18 | 0 | 0
9 | Loading and removal of excess material excavated from the trench and its transportation to a landfill at a distance of up to 10km. Calculation per m3 | m3 | 6.5 | 0 | 0
|  | Total IV: |  |  | 0
TOTAL: |  |  |  |  | 0
5.2 Storm water sewer Branch 2- Section ARSH 21- ARSH 17
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 99.97 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 99.03m3 of which:
| Mechanical excavation 80% | m3 | 79.224 | 0 | 0
| Manual excavation 20% | m3 | 19.806 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 99.97 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 56.82 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 42.21 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 315 mm | m | 99.97 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 20.8 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 10.4 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 67.22 | 0 | 0
9 | Procurement, transport and installation of reinforced concrete sewer inspection and inspection-cascade manholes with a diameter of ID1000 mm, which are composed of elements (cone, extension and bottom). The price includes the installation of metal climbing frames in the manhole. The manholes must have a reinforced concrete ring to accept vertical loads. The manhole cover must be cast iron, heavy type (400 kg). The calculation includes excavation and removal of excess soil to a landfill located up to L= 5 km away.
| 1.0 - 1.5m | piece | 4 | 0 | 0
TOTAL II: |  |  |  |  | 0
3. CONNECTION OF DRAINS AND GRIDS FOR ATM. SEWERAGE
1 | Excavation of soil of category III and IV for a trench, with a width of 0.8m and a depth of 0-2.0m, total V = 72m3 of which:
| mechanical 80% | m3 | 57.6 | 0 | 0
| manual 20% | m3 | 14.4 | 0 | 0
2 | Bottom planning accuracy + -2sm | m2 | 12 | 0 | 0
3 | Procurement and spreading of sand along the bottom of the trench to a thickness of 10cm. | m3 | 5.76 | 0 | 0
4 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 160 mm | m' | 60 | 0 | 0
| DN 200 mm | m' | 15 | 0 | 0
5 | Backfilling the trench in layers up to 30 cm above the top of the pipe with sand, by manual compaction. | m3 | 27.64 | 0 | 0
6 | Backfilling the trench in layers of 30cm with gravelly sandy material from the site (natural or crushed stone), with manual or mechanical compaction. | m3 | 38.6 | 0 | 0
7 | Construction of a street drain for storm water on a concrete base d=15cm together with a cast iron grate min. 500x500 straight shape, construction height min. 150 mm, external dimensions of the frame min. 500 x 500 mm. Load class min. D 400 according to EN124. (or equivalent) | piece | 3 | 0 | 0
8 | Procurement, transport and installation of a linear drainage channel made of polymer concrete, with dimensions L=100 cm, B=19cm; H=21 cm; galvanized steel edge, complete with cast grating with load class D400 in accordance with EN 1433. The price should also include end plates. | piece | 6 | 0 | 0
9 | Loading and removal of excess material excavated from the trench and its transportation to a landfill at a distance of up to 10km. Calculation per m3 | m3 | 38.6 | 0 | 0
TOTAL III: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
5.3 Storm water sewer Branch 3 Section ARSH22-ARSH11
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 111.53 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 159m3 of which:
| Mechanical excavation 80% | m3 | 127.272 | 0 | 0
| Manual excavation 20% | m3 | 31.818 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 111.53 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 63.39 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 95.7 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing. |  |  | 0
| DN 315 mm | m | 99.97 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 20.8 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 10.4 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 73.79 | 0 | 0
9 | Procurement, transport and installation of reinforced concrete sewer inspection and inspection-cascade manholes with a diameter of ID1000 mm, which are composed of elements (cone, extension and bottom). The price includes the installation of metal climbing frames in the manhole. The manholes must have a reinforced concrete ring to accept vertical loads. The manhole cover must be cast iron, heavy type (400 kg). The calculation includes excavation and removal of excess soil to a landfill located up to L= 5 km away.
| 1.0 - 1.5m | piece | 4 | 0 | 0
TOTAL II: |  |  |  |  | 0
3. CONNECTION OF DRAINS AND GRIDS FOR ATM. SEWERAGE
1 | Excavation of soil of category III and IV for a trench, with a width of 0.8m and a depth of 0-2.0m, total V = 14.4m3 of which:
| mechanical 80% | m3 | 11.52 | 0 | 0
| manual 20% | m3 | 2.88 | 0 | 0
2 | Bottom planning accuracy + -2sm | m2 | 12 | 0 | 0
3 | Procurement and spreading of sand along the bottom of the trench to a thickness of 10cm. | m3 | 1.2 | 0 | 0
4 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 200 mm | m' | 15 | 0 | 0
5 | Backfilling the trench in layers up to 30 cm above the top of the pipe with sand, by manual compaction. | m3 | 3.64 | 0 | 0
6 | Backfilling the trench in layers of 30cm with gravelly sandy material from the site (natural or crushed stone), with manual or mechanical compaction. | m3 | 10.16 | 0 | 0
7 | Construction of a street drain for storm water on a concrete base d=15cm together with a cast iron grate min. 500x500 straight shape, construction height min. 150 mm, external dimensions of the frame min. 500 x 500 mm. Load class min. D 400 according to EN124. (or equivalent) | piece | 5 | 0 | 0
8 | Loading and removal of excess material excavated from the trench and its transportation to a landfill at a distance of up to 10km. Calculation per m3 | m3 | 10.16 | 0 | 0
|  | Total III: |  |  | 0
TOTAL: |  |  |  |  | 0
5.4 Storm water sewer Branch 4 Section ARSH 26- ARSH 24
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 39.74 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 49.79m3 of which:
| Mechanical excavation 80% | m3 | 39.832 | 0 | 0
| Manual excavation 20% | m3 | 9.958 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 39.74 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 23 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 26.79 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing. |  |  | 0
| DN 315 mm | m | 47 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 10.4 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 5.2 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 28.2 | 0 | 0
9 | Procurement, transport and installation of reinforced concrete sewer inspection and inspection-cascade manholes with a diameter of ID1000 mm, which are composed of elements (cone, extension and bottom). The price includes the installation of metal climbing frames in the manhole. The manholes must have a reinforced concrete ring to accept vertical loads. The manhole cover must be cast iron, heavy type (400 kg). The calculation includes excavation and removal of excess soil to a landfill located up to L= 5 km away.
| 1.0 - 1.5m | piece | 2 | 0 | 0
TOTAL II: |  |  |  |  | 0
3. CONNECTION OF DRAINS AND GRIDS FOR ATM. SEWERAGE
1 | Excavation of soil of category III and IV for a trench, with a width of 0.8m and a depth of 0-2.0m, total V = 9.6m3 of which:
| mechanical 80% | m3 | 7.68 | 0 | 0
| manual 20% | m3 | 1.92 | 0 | 0
2 | Bottom planning accuracy + -2sm | m2 | 8 | 0 | 0
3 | Procurement and spreading of sand along the bottom of the trench to a thickness of 10cm. | m3 | 1.2 | 0 | 0
4 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 200 mm | m' | 10 | 0 | 0
5 | Backfilling the trench in layers up to 30 cm above the top of the pipe with sand, by manual compaction. | m3 | 5.68 | 0 | 0
6 | Backfilling the trench in layers of 30cm with gravelly sandy material from the site (natural or crushed stone), with manual or mechanical compaction. | m3 | 2.72 | 0 | 0
7 | Construction of a street drain for storm water on a concrete base d=15cm together with a cast iron grate min. 500x500 straight shape, construction height min. 150 mm, external dimensions of the frame min. 500 x 500 mm. Load class min. D 400 according to EN124. (or equivalent) | piece | 2 | 0 | 0
8 | Loading and removal of excess material excavated from the trench and its transportation to a landfill at a distance of up to 10km. Calculation per m3 | m3 | 2.72 | 0 | 0
|  | Total III: |  |  | 0
TOTAL: |  |  |  |  | 0
5.5 Storm water sewer Branch 5 Section ARSH 28-ARSH 9
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 46.97 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 57.01m3 of which:
| Mechanical excavation 80% | m3 | 45.608 | 0 | 0
| Manual excavation 20% | m3 | 11.402 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 46.97 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 26.69 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 30.32 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 315 mm | m | 47 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 10.4 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 5.2 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 31.89 | 0 | 0
9 | Procurement, transport and installation of reinforced concrete sewer inspection and inspection-cascade manholes with a diameter of ID1000 mm, which are composed of elements (cone, extension and bottom). The price includes the installation of metal climbing frames in the manhole. The manholes must have a reinforced concrete ring to accept vertical loads. The manhole cover must be cast iron, heavy type (400 kg). The calculation includes excavation and removal of excess soil to a landfill located up to L= 5 km away.
| 1.0 - 1.5m | piece | 2 | 0 | 0
TOTAL II: |  |  |  |  | 0
3. CONNECTION OF DRAINS AND GRIDS FOR ATM. SEWERAGE
1 | Excavation of soil of category III and IV for a trench, with a width of 0.8m and a depth of 0-2.0m, total V = 9.6m3 of which:
| mechanical 80% | m3 | 7.68 | 0 | 0
| manual 20% | m3 | 1.92 | 0 | 0
2 | Bottom planning accuracy + -2sm | m2 | 8 | 0 | 0
3 | Procurement and spreading of sand along the bottom of the trench to a thickness of 10cm. | m3 | 1.2 | 0 | 0
4 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 200 mm | m' | 10 | 0 | 0
5 | Backfilling the trench in layers up to 30 cm above the top of the pipe with sand, by manual compaction. | m3 | 5.68 | 0 | 0
6 | Backfilling the trench in layers of 30cm with gravelly sandy material from the site (natural or crushed stone), with manual or mechanical compaction. | m3 | 2.72 | 0 | 0
7 | Construction of a street drain for storm water on a concrete base d=15cm together with a cast iron grate min. 500x500 straight shape, construction height min. 150 mm, external dimensions of the frame min. 500 x 500 mm. Load class min. D 400 according to EN124. (or equivalent) | piece | 2 | 0 | 0
8 | Loading and removal of excess material excavated from the trench and its transportation to a landfill at a distance of up to 10km. Calculation per m3 | m3 | 2.72 | 0 | 0
|  | Total III: |  |  | 0
TOTAL: |  |  |  |  | 0
5.6 Storm water sewer Branch 6 Section ARSH30-ARSH 39
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 185.2 | 0 | 0
TOTAL I:
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 246m3 of which:
| Mechanical excavation 80% | m3 | 196.8 | 0 | 0
| Manual excavation 20% | m3 | 49.2 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 185.2 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 105.27 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 140.73 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing. |  |  | 0
| DN 315 mm | m | 185.2 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 46.8 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 23.4 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 128.67 | 0 | 0
9 | Procurement, transport and installation of reinforced concrete sewer inspection and inspection-cascade manholes with a diameter of ID1000 mm, which are composed of elements (cone, extension and bottom). The price includes the installation of metal climbing frames in the manhole. The manholes must have a reinforced concrete ring to accept vertical loads. The manhole cover must be cast iron, heavy type (400 kg). The calculation includes excavation and removal of excess soil to a landfill located up to L= 5 km away.
| 1.0 - 1.5m | piece | 9 | 0 | 0
TOTAL II: |  |  |  |  | 0
3. CONNECTION OF DRAINS AND GRIDS FOR ATM. SEWERAGE
1 | Excavation of soil of category III and IV for a trench, with a width of 0.8m and a depth of 0-2.0m, total V = 153.6m3 of which:
| mechanical 80% | m3 | 7.68 | 0 | 0
| manual 20% | m3 | 1.92 | 0 | 0
2 | Bottom planning accuracy + -2sm | m2 | 64 | 0 | 0
3 | Procurement and spreading of sand along the bottom of the trench to a thickness of 10cm. | m3 | 1.2 | 0 | 0
4 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 200 mm | m' | 80 | 0 | 0
| DN 160 mm | m' | 80 | 0 | 0
5 | Backfilling the trench in layers up to 30 cm above the top of the pipe with sand, by manual compaction. | m3 | 64 | 0 | 0
6 | Backfilling the trench in layers of 30cm with gravelly sandy material from the site (natural or crushed stone), with manual or mechanical compaction. | m3 | 88.4 | 0 | 0
7 | Construction of a street drain for storm water on a concrete base d=15cm together with a cast iron grate min. 500x500 straight shape, construction height min. 150 mm, external dimensions of the frame min. 500 x 500 mm. Load class min. D 400 according to EN124. (or equivalent) | piece | 12 | 0 | 0
8 | Procurement, transport and installation of a linear drainage channel made of polymer concrete, with dimensions L=100 cm, B=19cm; H=21 cm; galvanized steel edge, complete with cast grating with load class D400 in accordance with EN 1433. The price should also include end plates. | piece | 5 | 0 | 0
9 | Loading and removal of excess material excavated from the trench and its transportation to a landfill at a distance of up to 10km. Calculation per m3 | m3 | 88.4 | 0 | 0
|  | Total III: |  |  | 0
TOTAL: |  |  |  |  | 0
5.7 Storm water sewer Branch 7 Section ARSH 40- to outlet 2
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 217.38 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 387.05m3 of which:
| Mechanical excavation 80% | m3 | 309.64 | 0 | 0
| Manual excavation 20% | m3 | 77.41 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 217.38 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 120.54 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 266.51 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing. |  |  | 0
| DN 315 mm | m | 80.06 | 0 | 0
| DN 400 mm | m | 57.32 | 0 | 0
| DN 500 mm | m | 80 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 46.8 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 23.4 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 143.94 | 0 | 0
9 | Procurement, transportation and installation of reinforced concrete sewer inspection and inspection-cascade manholes with a diameter of ID1000 mm, which are composed of elements (cone, extension and bottom). The price includes the installation of metal climbing frames in the manhole. The manholes must have a reinforced concrete ring to accept vertical loads. The manhole cover must be cast iron, heavy type (400 kg).
| 1.0 - 1.5m | piece | 3 | 0 | 0
| 1.5 - 2.0m | piece | 7 | 0 | 0
10 | Procurement, transportation and installation of an oil separator with a capacity of Qmax = 200 l/s, with a 10% bypass. The separator shall be supplied with a coalescent filter, an inspection area and sampling for testing the treated water. The price shall also include inspection covers for the separator. | piece | 1 | 0 | 0
TOTAL II: |  |  |  |  | 0
3.DISCHARGE INTO A CANAL
3.1 ASSEMBLY WORKS
1 | Procurement, transportation and installation of a frog cover on the outlet of the storm sewer. Calculation per piece. DN 500 | piece | 1 | 0 | 0
TOTAL : |  |  |  |  | 0
3.2 CONCRETE WORKS
1 | Procurement, transportation and installation of reinforced concrete C30/37 for the construction of a drain. | m3 | 2.56 | 0 | 0
2 | Procurement, transportation and installation of lean concrete C12/15 as a base for installing the drain. | m3 | 0.7 | 0 | 0
TOTAL: |  |  |  |  | 0
3.3 REINFORCEMENT WORKS
1 | Procurement, transportation and installation of B500B reinforcement according to technical specifications. | kg | 275 | 0 | 0
TOTAL : |  |  |  |  | 0
TOTAL III: |  |  |  |  | 0
4. CONNECTION OF DRAINS AND GRIDS FOR ATM. SEWERAGE
1 | Excavation of soil of category III and IV for a trench, with a width of 0.8m and a depth of 0-2.0m, total V = 211.2m3 of which:
| mechanical 80% | m3 | 168.96 | 0 | 0
| manual 20% | m3 | 42.24 | 0 | 0
2 | Bottom planning accuracy + -2sm | m2 | 16 | 0 | 0
3 | Procurement and spreading of sand along the bottom of the trench to a thickness of 10cm. | m3 | 16.896 | 0 | 0
4 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 200 mm | m' | 200 | 0 | 0
| DN 160 mm | m' | 20 | 0 | 0
5 | Backfilling the trench in layers up to 30 cm above the top of the pipe with sand, by manual compaction. | m3 | 88 | 0 | 0
6 | Backfilling the trench in layers of 30cm with gravelly sandy material from the site (natural or crushed stone), with manual or mechanical compaction. | m3 | 106.304 | 0 | 0
7 | Construction of a street drain for storm water on a concrete base d=15cm together with a cast iron grate min. 500x500 straight shape, construction height min. 150 mm, external dimensions of the frame min. 500 x 500 mm. Load class min. D 400 according to EN124. (or equivalent) | piece | 7 | 0 | 0
8 | Procurement, transport and installation of a linear drainage channel made of polymer concrete, with dimensions L=1000cm, B=19cm; H=21 cm; galvanized steel edge, complete with cast grating with load class D400 in accordance with EN 1433. The price should also include end plates. | piece | 21 | 0 | 0
9 | Loading and removal of excess material excavated from the trench and its transportation to a landfill at a distance of up to 10km. Calculation per m3 | m3 | 48.704 | 0 | 0
|  | Total VI: |  |  | 0
TOTAL: |  |  |  |  | 0
5.8 Storm water sewer Branch 8 Section ARSH 48- ARSH 43
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 54.06 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 68.14m3 of which:
| Mechanical excavation 80% | m3 | 54.512 | 0 | 0
| Manual excavation 20% | m3 | 13.628 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 54.06 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 27.76 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 40.38 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing. |  |  | 0
| DN 315 mm | m | 54.06 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 10.4 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 5.2 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 32.96 | 0 | 0
9 | Procurement, transportation and installation of reinforced concrete sewer inspection and inspection-cascade manholes with a diameter of ID1000 mm, which are composed of elements (cone, extension and bottom). The price includes the installation of metal climbing frames in the manhole. The manholes must have a reinforced concrete ring to accept vertical loads. The manhole cover must be cast iron, heavy type (400 kg).
| 1.0 - 1.5m | piece | 2 | 0 | 0
TOTAL II: |  |  |  |  | 0
3. CONNECTION OF DRAINS AND GRIDS FOR ATM. SEWERAGE
1 | Excavation of soil of category III and IV for a trench, with a width of 0.8m and a depth of 0-2.0m, total V = 96m3 of which:
| mechanical 80% | m3 | 76.8 | 0 | 0
| manual 20% | m3 | 19.2 | 0 | 0
2 | Bottom planning accuracy + -2sm | m2 | 32 | 0 | 0
3 | Procurement and spreading of sand along the bottom of the trench to a thickness of 10cm. | m3 | 7.68 | 0 | 0
4 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 200 mm | m' | 60 | 0 | 0
| DN 160 mm | m' | 40 | 0 | 0
5 | Backfilling the trench in layers up to 30 cm above the top of the pipe with sand, by manual compaction. | m3 | 38 | 0 | 0
6 | Backfilling the trench in layers of 30cm with gravelly sandy material from the site (natural or crushed stone), with manual or mechanical compaction. | m3 | 50.32 | 0 | 0
7 | Construction of a street drain for storm water on a concrete base d=15cm together with a cast iron grate min. 500x500 straight shape, construction height min. 150 mm, external dimensions of the frame min. 500 x 500 mm. Load class min. D 400 according to EN124. (or equivalent) | piece | 4 | 0 | 0
8 | Loading and removal of excess material excavated from the trench and its transportation to a landfill at a distance of up to 10km. Calculation per m3 | m3 | 50.32 | 0 | 0
|  | Total III: |  |  | 0
TOTAL: |  |  |  |  | 0
5.9 Storm water sewer Branch 9 Section ARSH 50- ARSH 45
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 92.03 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 194.53m3 of which:
| Mechanical excavation 80% | m3 | 155.624 | 0 | 0
| Manual excavation 20% | m3 | 38.906 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 92.03 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 39.5 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 155.03 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing. |  |  | 0
| DN 315 mm | m | 92.03 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 10.4 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 5.2 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 44.7 | 0 | 0
9 | Procurement, transportation and installation of reinforced concrete sewer inspection and inspection-cascade manholes with a diameter of ID1000 mm, which are composed of elements (cone, extension and bottom). The price includes the installation of metal climbing frames in the manhole. The manholes must have a reinforced concrete ring to accept vertical loads. The manhole cover must be cast iron, heavy type (400 kg).
| 1.0 - 1.5m | piece | 6 | 0 | 0
TOTAL II: |  |  |  |  | 0
3. CONNECTION OF DRAINS AND GRIDS FOR ATM. SEWERAGE
1 | Excavation of soil of category III and IV for a trench, with a width of 0.8m and a depth of 0-2.0m, total V = 57.6m3 of which:
| mechanical 80% | m3 | 46.08 | 0 | 0
| manual 20% | m3 | 11.52 | 0 | 0
2 | Bottom planning accuracy + -2sm | m2 | 24 | 0 | 0
3 | Procurement and spreading of sand along the bottom of the trench to a thickness of 10cm. | m3 | 4.8 | 0 | 0
4 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 200 mm | m' | 40 | 0 | 0
| DN 160 mm | m' | 30 | 0 | 0
5 | Backfilling the trench in layers up to 30 cm above the top of the pipe with sand, by manual compaction. | m3 | 9.7 | 0 | 0
6 | Backfilling the trench in layers of 30cm with gravelly sandy material from the site (natural or crushed stone), with manual or mechanical compaction. | m3 | 43.1 | 0 | 0
7 | Construction of a street drain for storm water on a concrete base d=15cm together with a cast iron grate min. 500x500 straight shape, construction height min. 150 mm, external dimensions of the frame min. 500 x 500 mm. Load class min. D 400 according to EN124. (or equivalent) | piece | 4 | 0 | 0
8 | Procurement, transport and installation of a linear drainage channel made of polymer concrete, with dimensions L=100 cm, B=19cm; H=21 cm; galvanized steel edge, complete with cast grating with load class D400 in accordance with EN 1433. The price should also include end plates. | piece | 3 | 0 | 0
9 | Loading and removal of excess material excavated from the trench and its transportation to a landfill at a distance of up to 10km. Calculation per m3 | m3 | 43.1 | 0 | 0
|  | Total III: |  |  | 0
TOTAL: |  |  |  |  | 0
5.10 Storm water sewer Branch 10 Section ARSH 59- ARSH 54
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 38.94 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 42.4m3 of which:
| Mechanical excavation 80% | m3 | 33.92 | 0 | 0
| Manual excavation 20% | m3 | 8.48 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 38.94 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 22.06 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 20.34 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 315 mm | m | 39 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 10.4 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 5.2 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 27.26 | 0 | 0
9 | Procurement, transportation and installation of reinforced concrete sewer inspection and inspection-cascade manholes with a diameter of ID1000 mm, which are composed of elements (cone, extension and bottom). The price includes the installation of metal climbing frames in the manhole. The manholes must have a reinforced concrete ring to accept vertical loads. The manhole cover must be cast iron, heavy type (400 kg).
| 1.0 - 1.5m | piece | 2 | 0 | 0
TOTAL II: |  |  |  |  | 0
3. CONNECTION OF DRAINS AND GRIDS FOR ATM. SEWERAGE
1 | Excavation of soil of category III and IV for a trench, with a width of 0.8m and a depth of 0-2.0m, total V = 24m3 of which:
| mechanical 80% | m3 | 19.2 | 0 | 0
| manual 20% | m3 | 4.8 | 0 | 0
2 | Bottom planning accuracy + -2sm | m2 | 20 | 0 | 0
3 | Procurement and spreading of sand along the bottom of the trench to a thickness of 10cm. | m3 | 2 | 0 | 0
4 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 160 mm | m' | 25 | 0 | 0
5 | Backfilling the trench in layers up to 30 cm above the top of the pipe with sand, by manual compaction. | m3 | 9.7 | 0 | 0
6 | Backfilling the trench in layers of 30cm with gravelly sandy material from the site (natural or crushed stone), with manual or mechanical compaction. | m3 | 12.3 | 0 | 0
7 | Construction of a street drain for storm water on a concrete base d=15cm together with a cast iron grate min. 500x500 straight shape, construction height min. 150 mm, external dimensions of the frame min. 500 x 500 mm. Load class min. D 400 according to EN124. (or equivalent) | piece | 3 | 0 | 0
8 | Loading and removal of excess material excavated from the trench and its transportation to a landfill at a distance of up to 10km. Calculation per m3 | m3 | 12.3 | 0 | 0
|  | Total III: |  |  | 0
TOTAL: |  |  |  |  | 0
5.11 Storm water sewer Branch 11 Section ARSH 57- ARSH 54
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 35.35 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 37.16m3 of which:
| Mechanical excavation 80% | m3 | 29.728 | 0 | 0
| Manual excavation 20% | m3 | 7.432 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 35.35 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 20.41 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 16.75 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 315 mm | m | 35.35 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 10.4 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 5.2 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 25.61 | 0 | 0
9 | Procurement, transportation and installation of reinforced concrete sewer inspection and inspection-cascade manholes with a diameter of ID1000 mm, which are composed of elements (cone, extension and bottom). The price includes the installation of metal climbing frames in the manhole. The manholes must have a reinforced concrete ring to accept vertical loads. The manhole cover must be cast iron, heavy type (400 kg).
| 1.0 - 1.5m | piece | 2 | 0 | 0
TOTAL II: |  |  |  |  | 0
3. CONNECTION OF DRAINS AND GRIDS FOR ATM. SEWERAGE
1 | Excavation of soil of category III and IV for a trench, with a width of 0.8m and a depth of 0-2.0m, total V = 24m3 of which:
| mechanical 80% | m3 | 19.2 | 0 | 0
| manual 20% | m3 | 4.8 | 0 | 0
2 | Bottom planning accuracy + -2sm | m2 | 20 | 0 | 0
3 | Procurement and spreading of sand along the bottom of the trench to a thickness of 10cm. | m3 | 2 | 0 | 0
4 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 160 mm | m' | 25 | 0 | 0
5 | Backfilling the trench in layers up to 30 cm above the top of the pipe with sand, by manual compaction. | m3 | 9.7 | 0 | 0
6 | Backfilling the trench in layers of 30cm with gravelly sandy material from the site (natural or crushed stone), with manual or mechanical compaction. | m3 | 12.3 | 0 | 0
7 | Construction of a street drain for storm water on a concrete base d=15cm together with a cast iron grate min. 500x500 straight shape, construction height min. 150 mm, external dimensions of the frame min. 500 x 500 mm. Load class min. D 400 according to EN124. (or equivalent) | piece | 3 | 0 | 0
8 | Loading and removal of excess material excavated from the trench and its transportation to a landfill at a distance of up to 10km. Calculation per m3 | m3 | 12.3 | 0 | 0
|  | Total III: |  |  | 0
TOTAL: |  |  |  |  | 0
5.12 Storm water sewer Branch 12 Section ARSH 55- ARSH 52
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 32.25 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 41.17m3 of which:
| Mechanical excavation 80% | m3 | 32.936 | 0 | 0
| Manual excavation 20% | m3 | 8.234 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 32.25 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 18.32 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 22.85 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 315 mm | m | 32 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 10.4 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 5.2 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 23.52 | 0 | 0
9 | Procurement, transportation and installation of reinforced concrete sewer inspection and inspection-cascade manholes with a diameter of ID1000 mm, which are composed of elements (cone, extension and bottom). The price includes the installation of metal climbing frames in the manhole. The manholes must have a reinforced concrete ring to accept vertical loads. The manhole cover must be cast iron, heavy type (400 kg).
| 1.0 - 1.5m | piece | 2 | 0 | 0
TOTAL II: |  |  |  |  | 0
3. CONNECTION OF DRAINS AND GRIDS FOR ATM. SEWERAGE
1 | Excavation of soil of category III and IV for a trench, with a width of 0.8m and a depth of 0-2.0m, total V = 48m3 of which:
| mechanical 80% | m3 | 38.4 | 0 | 0
| manual 20% | m3 | 9.6 | 0 | 0
2 | Bottom planning accuracy + -2sm | m2 | 8 | 0 | 0
3 | Procurement and spreading of sand along the bottom of the trench to a thickness of 10cm. | m3 | 3.84 | 0 | 0
4 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 200 mm | m' | 40 | 0 | 0
| DN 160 mm | m' | 10 | 0 | 0
5 | Backfilling the trench in layers up to 30 cm above the top of the pipe with sand, by manual compaction. | m3 | 9.7 | 0 | 0
6 | Backfilling the trench in layers of 30cm with gravelly sandy material from the site (natural or crushed stone), with manual or mechanical compaction. | m3 | 34.46 | 0 | 0
7 | Construction of a street drain for storm water on a concrete base d=15cm together with a cast iron grate min. 500x500 straight shape, construction height min. 150 mm, external dimensions of the frame min. 500 x 500 mm. Load class min. D 400 according to EN124. (or equivalent) | piece | 2 | 0 | 0
8 | Procurement, transport and installation of a linear drainage channel made of polymer concrete, with dimensions L=100 cm, B=19cm; H=21 cm; galvanized steel edge, complete with cast grating with load class D400 in accordance with EN 1433. The price should also include end plates. | piece | 3 | 0 | 0
9 | Loading and removal of excess material excavated from the trench and its transportation to a landfill at a distance of up to 10km. Calculation per m3 | m3 | 34.46 | 0 | 0
|  | Total III: |  |  | 0
TOTAL: |  |  |  |  | 0
6. External storm water sewer from gutters
6.1 Storm water sewer from gutters Branch 1 Section ASH1-ASH20
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 100.33 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 75.96m3 of which:
| Mechanical excavation 80% | m3 | 60.768 | 0 | 0
| Manual excavation 20% | m3 | 15.192 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 80.264 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 55.03 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 20.93 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 160 mm | m | 20 | 0 | 0
| DN 200 mm | m | 100 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 28 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 14 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 69.03 | 0 | 0
9 | Procurement and installation of reinforced concrete manholes (monoliths) with a clear opening of 600 mm with a wall and slab thickness of 20 cm, average manhole height up to H=1.0 m with a cast iron cover D=160 kg for heavy traffic and dimensions according to the details given in the graphic section | piece | 8 | 0 | 0
TOTAL II: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
6.2 Storm water sewer from gutters Branch 2 Section ASH13-ASH10
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 144.95 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 117.96m3 of which:
| Mechanical excavation 80% | m3 | 94.368 | 0 | 0
| Manual excavation 20% | m3 | 23.592 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 115.96 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 79.59 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 38.1 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 160 mm | m | 20 | 0 | 0
| DN 200 mm | m | 85.43 | 0 | 0
| DN 315 mm | m | 59.52 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 36 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 18 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 97.59 | 0 | 0
9 | Procurement and installation of reinforced concrete manholes (monoliths) with a clear opening of 600 mm with a wall and slab thickness of 20 cm, average manhole height up to H=1.0 m with a cast iron cover D=160 kg for heavy traffic and dimensions according to the details given in the graphic section | piece | 7 | 0 | 0
TOTAL II: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
6.3 Storm water sewer from gutters Branch 3 Section ASH7- to Outlet2
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 123.95 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 114.25m3 of which:
| Mechanical excavation 80% | m3 | 91.96 | 0 | 0
| Manual excavation 20% | m3 | 22.99 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 99.16 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 67.91 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 46.34 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 200 mm | m | 53.23 | 0 | 0
| DN 315 mm | m | 70.72 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 20 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 10 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 77.91 | 0 | 0
9 | Procurement and installation of reinforced concrete manholes (monoliths) with a clear opening of 600 mm with a wall and slab thickness of 20 cm, average manhole height up to H=1.0 m with a cast iron cover D=160 kg for heavy traffic and dimensions according to the details given in the graphic section | piece | 5 | 0 | 0
TOTAL II: |  |  |  |  | 0
3.DISCHARGE INTO A CANAL
3.1 ASSEMBLY WORKS
1 | Procurement, transportation and installation of a frog cover on the outlet of the storm sewer. Calculation per piece. DN 315 mm | piece | 1 | 0 | 0
TOTAL : |  |  |  |  | 0
3.2 CONCRETE WORKS
1 | Procurement, transportation and installation of reinforced concrete C30/37 for the construction of a drain. | m3 | 2.56 | 0 | 0
2 | Procurement, transportation and installation of lean concrete C12/15 as a base for installing the drain. | m3 | 0.7 | 0 | 0
TOTAL : |  |  |  |  | 0
3.3 REINFORCEMENT WORKS
1 | Procurement, transportation and installation of B500B reinforcement according to technical specifications. | kg | 275 | 0 | 0
TOTAL : |  |  |  |  | 0
TOTAL III: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
6.4 Storm water sewer from gutters Branch 4 Section ASH65-ASH11
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 27.14 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 29.14m3 of which:
| Mechanical excavation 80% | m3 | 23.312 | 0 | 0
| Manual excavation 20% | m3 | 5.828 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 21.712 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 14.88 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 14.26 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 160 mm | m | 28 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 4 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 2 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 16.88 | 0 | 0
9 | Procurement and installation of reinforced concrete manholes (monoliths) with a clear opening of 600 mm with a wall and slab thickness of 20 cm, average manhole height up to H=1.0 m with a cast iron cover D=160 kg for heavy traffic and dimensions according to the details given in the graphic section | piece | 1 | 0 | 0
TOTAL II: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
6.5 Storm water sewer from gutters Branch 5 Section ASH59-ASH9
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 22.63 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 21.34m3 of which:
| Mechanical excavation 80% | m3 | 17.072 | 0 | 0
| Manual excavation 20% | m3 | 4.268 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 18.104 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 13.35 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 7.99 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 160 mm | m | 28 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 4 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 2 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 15.35 | 0 | 0
9 | Procurement and installation of reinforced concrete manholes (monoliths) with a clear opening of 600 mm with a wall and slab thickness of 20 cm, average manhole height up to H=1.0 m with a cast iron cover D=160 kg for heavy traffic and dimensions according to the details given in the graphic section | piece | 1 | 0 | 0
TOTAL II: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
6.6 Storm water sewer from gutters Branch 5 Section AS 55-AS 10
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 25.44 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 28.59m3 of which:
| Mechanical excavation 80% | m3 | 22.872 | 0 | 0
| Manual excavation 20% | m3 | 5.718 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 20.352 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 15.01 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 6.33 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 160 mm | m | 25 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 4 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 2 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 17.01 | 0 | 0
9 | Procurement and installation of reinforced concrete manholes (monoliths) with a clear opening of 600 mm with a wall and slab thickness of 20 cm, average manhole height up to H=1.0 m with a cast iron cover D=160 kg for heavy traffic and dimensions according to the details given in the graphic section | piece | 1 | 0 | 0
TOTAL II: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
6.7 Storm water sewer from gutters Branch 5 Section AS 42-AS 31
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 151.52 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 152.25m3 of which:
| Mechanical excavation 80% | m3 | 121.8 | 0 | 0
| Manual excavation 20% | m3 | 30.45 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 121.216 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 80.91 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 71.34 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 160 mm | m | 30 | 0 | 0
| DN 200 mm | m | 65.35 | 0 | 0
| DN 250 mm | m | 86.17 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 36 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 18 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 98.91 | 0 | 0
9 | Procurement and installation of reinforced concrete manholes (monoliths) with a clear opening of 600 mm with a wall and slab thickness of 20 cm, average manhole height up to H=1.0 m with a cast iron cover D=160 kg for heavy traffic and dimensions according to the details given in the graphic section | piece | 9 | 0 | 0
TOTAL II: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
6.8 Storm water sewer from gutters Branch 5 Section ASH52-ASH 30
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 155.95 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 157.95m3 of which:
| Mechanical excavation 80% | m3 | 126.36 | 0 | 0
| Manual excavation 20% | m3 | 31.59 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 124.76 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 85.48 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 72.47 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 160 mm | m | 30 | 0 | 0
| DN 200 mm | m | 65.35 | 0 | 0
| DN 250 mm | m | 90.6 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 36 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 18 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 103.48 | 0 | 0
9 | Procurement and installation of reinforced concrete manholes (monoliths) with a clear opening of 600 mm with a wall and slab thickness of 20 cm, average manhole height up to H=1.0 m with a cast iron cover D=160 kg for heavy traffic and dimensions according to the details given in the graphic section | piece | 10 | 0 | 0
TOTAL II: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
6.9 Storm water sewer from gutters Branch 5 Section AS 31 to outlet
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 103.73 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 1.0m and a depth of 0-2.0m, total V = 102.66m3 of which:
| Mechanical excavation 80% | m3 | 82.128 | 0 | 0
| Manual excavation 20% | m3 | 20.532 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 82.984 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 56.9 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 45.76 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 250 mm | m | 32.21 | 0 | 0
| DN 315 mm | m | 71.52 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 20 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 10 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 66.9 | 0 | 0
9 | Procurement and installation of reinforced concrete manholes (monoliths) with a clear opening of 600 mm with a wall and slab thickness of 20 cm, average manhole height up to H=1.0 m with a cast iron cover D=160 kg for heavy traffic and dimensions according to the details given in the graphic section | piece | 5 | 0 | 0
TOTAL II: |  |  |  |  | 0
3.DISCHARGE INTO A CANAL
3.1 ASSEMBLY WORKS
1 | Procurement, transportation and installation of a frog cover on the outlet of the storm sewer. Calculation per piece. DN 300 mm | piece | 1 | 0 | 0
TOTAL : |  |  |  |  | 0
3.2 CONCRETE WORKS
1 | Procurement, transportation and installation of reinforced concrete C30/37 for the construction of a drain. | m3 | 2.56 | 0 | 0
2 | Procurement, transportation and installation of lean concrete C12/15 as a base for installing the drain. | m3 | 0.7 | 0 | 0
TOTAL : |  |  |  |  | 0
3.3 REINFORCEMENT WORKS
1 | Procurement, transportation and installation of B500B reinforcement according to technical specifications. | kg | 275 | 0 | 0
TOTAL : |  |  |  |  | 0
TOTAL III: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
6.10 Storm water sewer from gutters Branch 10 Section ASH38-ASH 32
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 72.08 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 0.8m and a depth of 0-2.0m, total V = 54.08m3 of which:
| Mechanical excavation 80% | m3 | 43.776 | 0 | 0
| Manual excavation 20% | m3 | 10.944 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 57.664 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 39.54 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 15.18 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 200 mm | m | 72.08 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 20 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 10 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 49.54 | 0 | 0
9 | Procurement and installation of reinforced concrete manholes (monoliths) with a clear opening of 600 mm with a wall and slab thickness of 20 cm, average manhole height up to H=1.0 m with a cast iron cover D=160 kg for heavy traffic and dimensions according to the details given in the graphic section | piece | 5 | 0 | 0
TOTAL II: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
6.11 Storm water sewer from gutters Branch 11 Section ASH40-ASH39
1. GEODETIC WORKS
1 | Geodetic marking of the pipeline route. Calculation per m' of marked route. | m' | 17.24 | 0 | 0
TOTAL I: |  |  |  |  | 0
2. EARTH WORKS
1 | Excavation of soil of category III and IV for a trench, with a width of 0.8m and a depth of 0-2.0m, total V = 12.33m3 of which:
| Mechanical excavation 80% | m3 | 9.864 | 0 | 0
| Manual excavation 20% | m3 | 2.466 | 0 | 0
2 | Fine planning of the trench bottom with level accuracy± 2 cm | m2 | 13.792 | 0 | 0
3 | Procurement, transportation and installation of sand with a grain size of 4 - 8 mm for the preparation of a base for laying a pipeline with a thickness of d= 10cm and around and above the pipe 30cm. Calculation per m3. | m3 | 9.45 | 0 | 0
4 | Backfilling of excavated material according to specification (maximum grain size dmax62mm) after completion of construction works, to the required level of road construction with mechanical compaction in layers of 30cm to the required compaction. Calculation per m3. | m3 | 2.88 | 0 | 0
5 | Procurement, transport and installation of corrugated PP-HM sewer pipes SN 16, in accordance with EN13476-3 and street sewerage with hydraulic testing.
| DN 160 mm | m | 17.24 | 0 | 0
6 | Excavation to widen the manhole trench in category III soil with disposal of the excavated material next to the trench (part will be used for backfilling) | m3 | 4 | 0 | 0
7 | Backfilling the space around the shaft with part of the excavated soil by compacting in layers | m3 | 2 | 0 | 0
8 | Removal of excess soil from excavation (from trenches and shafts) | m3 | 11.45 | 0 | 0
9 | Procurement and installation of reinforced concrete manholes (monoliths) with a clear opening of 600 mm with a wall and slab thickness of 20 cm, average manhole height up to H=1.0 m with a cast iron cover D=160 kg for heavy traffic and dimensions according to the details given in the graphic section | piece | 1 | 0 | 0
TOTAL II: |  |  |  |  | 0
TOTAL: |  |  |  |  | 0
TOTAL BILL OF QUANTITY SUMMARY
1 | OBJECT: WELL SHAFT |  |  |  | 0
2 | OBJECT: TANK WITH A VOLUME OF 100 m3 |  |  |  | 0
3 | OBJECT: EXTERNAL WATER SUPPLY NETWORK |  |  |  | 0
4 | FACILITY: EXTERNAL SEWERAGE NETWORK
4.1. | Branch 1 -section FRS 1-FRS 9,sectionFRS 15-FRS 3,section FRS 36-Outlet |  |  |  | 0
4.2. | Branch 2-Poteg FRŠ 10-FRŠ 2 |  |  |  | 0
4.3. | Branch 3 - Section FRS 21-FRS 2 |  |  |  | 0
4.4. | Branch 4-Section FRŠ 29-FRŠ 7 |  |  |  | 0
4.5. | Branch 5-Section FRŠ 26-FRŠ 21 |  |  |  | 0
4.6. | Branch 6-Section FRŠ 32-FRŠ 7 |  |  |  | 0
TOTAL FACILITY: EXTERNAL SEWERAGE NETWORK |  |  |  |  | 0
5 | OBJECT: STORM WATER SEWER
5.1. | Branch 1 Section ARSH1 - Outlet 1 |  |  |  | 0
5.2. | Branch 2- Section ARSH 21- ARSH 17 |  |  |  | 0
5.3. | Branch 3 Section ARSH22-ARSH11 |  |  |  | 0
5.4. | Branch 4 Section ARSH 26- ARSH 24 |  |  |  | 0
5.5. | Branch 5 Section ARSH 28-ARSH 9 |  |  |  | 0
5.6. | Branch 6 Section ARSH30-ARSH 39 |  |  |  | 0
5.7. | Branch 7 Section ARSH 40- to outlet 2 |  |  |  | 0
5.8. | Branch 8 Section ARSH 48- ARSH 43 |  |  |  | 0
5.9. | Branch 9 Section ARSH 50- ARSH 45 |  |  |  | 0
5.10. | Branch 10 Section ARSH 59- ARSH 54 |  |  |  | 0
5.11. | Branch 11 Section ARSH 57- ARSH 54 |  |  |  | 0
5.12. | Branch 12 Section ARSH 55- ARSH 52 |  |  |  | 0
TOTAL OBJECT: STORM WATER SEWER |  |  |  |  | 0
6 | OBJECT: STORM WATER SEWER FROM GUTTER
6.1. | Branch 1 Section ASH1-ASH20 |  |  |  | 0
6.2. | Branch 2 Section ASH13-ASH10 |  |  |  | 0
6.3. | Branch 3 Section ASH7- to Outlet2 |  |  |  | 0
6.4. | Branch 4 Section ASH65-ASH11 |  |  |  | 0
6.5. | Branch 5 Section ASH59-ASH9 |  |  |  | 0
6.6. | Branch 5 Section AS 55-AS 10 |  |  |  | 0
6.7. | Branch 5 Section AS 42-AS 31 |  |  |  | 0
6.8. | Branch 5 Section ASH52-ASH 30 |  |  |  | 0
6.9. | Branch 5 Section AS 31 to outlet |  |  |  | 0
6.10. | Branch 10 Section ASH38-ASH 32 |  |  |  | 0
6.11. | Branch 11 Section ASH40-ASH39 |  |  |  | 0
TOTAL OBJECT: STORM WATER SEWER FROM GUTTER |  |  |  |  | 0
TOTAL OF BILL OF QUANTITY CALCULATION [MKD] |  |  |  |  | 0
VAT 18% [MKD] |  |  |  |  | 0
TOTAL CALCULATION [MKD] |  |  |  |  | 0